## WAN
SN | Ticket No | W/O | Date | NOC WAN Engineer | Alert Type | Issue Type | Initial Findings | Node ID | Cabinet Asset Field Tag | Location | Coordinates | Area Category | Severity | Fault Notification Date and Time (dd/mm/yy hh:mm) | Fault Response Date and Time (dd/mm/yy hh:mm) | FRT Fault Response Time (Minutes) | Actual Start Date and Time (dd/mm/yy hh:mm) | Actual Finish Date and Time (dd/mm/yy hh:mm) | ART Active Repair Time (Minutes) | TRT Total Repair Time (Minutes) | Action Taken | Status | Fault Attribution | FA Class | FA (Fault Attraction) Notes | Remarks | Field Engineer
1 | NA | NA | 2026-02-01 | - | Node Down | Network down | FLM visited the site and confirmed that Kahramaa power was not available at the cabinet. | P010-ENC61-CE-01 |  | Zone 57 | 51.4699752, 25.170097 | Outside Doha | Critical | 2026-02-01 08:39 | 2026-02-01 08:39 | 0 | 2026-02-01 08:39 | 2026-02-01 13:57 | 318 | 318 | Power was restored by Kahramaa after 5 hours and 17 minutes.Network was up. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
2 | NA | NA | 2026-02-02 | - | Node Down | Network down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-02 13:04 | 2026-02-02 13:04 | 0 | 2026-02-02 13:04 | 2026-02-02 13:08 | 4 | 4 | Link restored after 4 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
3 | NA | NA | 2026-02-02 | - | Node Down | Network down | network went down due to system upgrade | P008C2-Enc09-CE01 |  | - | - | - | Critical | 2026-02-02 06:49 | 2026-02-02 06:49 | 0 | 2026-02-02 06:49 | 2026-02-02 06:50 | 1 | 1 | Escalated to Salam Tech team (Imran) on phone and rebooted the system | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
4 | NA | NA | 2026-02-04 | Vishnu | Node Down | Device Down | Power failure detected at the site | Sal-ENC38-CE-01 |  | Zone 83 | 51.1144427, 25.069908 | Outside Doha | Critical | 2026-02-04 07:00 | 2026-02-04 07:00 | 0 | 2026-02-04 08:00 | 2026-02-04 13:52 | 352 | 412 | The Kahramaa team is currently performing maintenance on the main electrical poles in the area.Expected Completion: Restoration is anticipated by 2:00 PM. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
5 | NA | NA | 2026-02-05 | - | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-05 12:47 | 2026-02-05 12:47 | 0 | 2026-02-05 12:47 | 2026-02-05 12:50 | 3 | 3 | Link restored after 3 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
6 | NA | NA | 2026-02-05 | - | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-05 14:25 | 2026-02-05 14:25 | 0 | 2026-02-05 14:25 | 2026-02-05 14:36 | 11 | 11 | Link restored after 11 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
7 | NA | NA | 2026-02-06 | Vishnu | Node Down | Device Down | UPS was not giving output | P010-ENC61–CE-01 |  | Zone 57 | 51.4699752, 25.170097 | Outside Doha | Critical | 2026-02-06 09:36 | 2026-02-06 09:36 | 0 | 2026-02-06 11:01 | 2026-02-06 11:08 | 7 | 92 | Issue resolved after restarting UPS | Completed | Maintainer | N/a | N/a | Network Back Online
8 | NA | NA | 2026-02-07 | Vishnu | Node Down | Device Down | Noticed no power on Main breakers/Terminals | P023C1-ENC01–CE -01 |  | Zone 91 | 51.583897, 25.111748 | Outside Doha | Critical | 2026-02-07 11:25 | 2026-02-07 11:25 | 0 | 2026-02-07 12:02 | 2026-02-07 13:13 | 71 | 108 | Power supply restored by Kahrama staff.Kharahma reference No. 261100005225 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
9 | NA | NA | 2026-02-07 | Vishnu | Node Down | Device Down | Noticed no power on Main breakers/Terminals | P023C1-ENC01–UPE -01 |  | Zone 91 | 51.583897, 25.111748 | Outside Doha | Critical | 2026-02-07 11:25 | 2026-02-07 11:25 | 0 | 2026-02-07 12:02 | 2026-02-07 13:13 | 71 | 108 | Power supply restored by Kahrama staff.Kharahma reference No. 261100005225 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
10 | NA | NA | 2026-02-08 | Salem/Amr | Node Down | Device Down | MCB was tripped at site | SAL-ENC50–CE -01 |  | Zone 96 | 50.9993542, 24.9513076 | Outside Doha | Critical | 2026-02-08 12:29 | 2026-02-08 12:29 | 0 | 2026-02-08 13:34 | 2026-02-08 14:00 | 26 | 91 | team turned on the CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online
11 | NA | NA | 2026-02-09 | Salem/Amr | Node Down | Device Down | Link went down | P008C3-ENC01–CE -01 |  | Zone 55 | 51.4801647, 25.2614822 | Outside Doha | Critical | 2026-02-09 15:06 | 2026-02-09 15:06 | 0 | 2026-02-09 15:06 | 2026-02-09 15:08 | 2 | 2 | Escalated to Salam Tech team (Imran) on phone and rebooted the system | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
12 | NA | NA | 2026-02-09 | Salem/Amr | Node Down | Device Down | Link went down | P008C3-ENC25–CE -01 |  | Zone 56 | 51.50261, 25.2341068 | Outside Doha | Critical | 2026-02-09 15:43 | 2026-02-09 15:43 | 0 | 2026-02-09 15:43 | 2026-02-09 15:45 | 2 | 2 | Escalated to Salam Tech team (Imran) on phone and rebooted the system | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
13 | NA | NA | 2026-02-10 | Salem/Amr | Node Down | Link Down | MCB was tripped at site | P005-ENC410-CE-01 |  | Zone 56 | 51.399465, 25.3102445 | Outside Doha | Critical | 2026-02-10 13:39 | 2026-02-10 13:39 | 0 | 2026-02-10 14:14 | 2026-02-10 15:52 | 98 | 133 | Team turned on the CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online
14 | NA | NA | 2026-02-10 | Salem/Amr | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-10 16:19 | 2026-02-10 16:19 | 0 | 2026-02-10 16:19 | 2026-02-10 16:26 | 7 | 7 | Link went down and restored after 7 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
15 | NA | NA | 2026-02-11 | Salem/Amr | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-11 12:59 | 2026-02-11 12:59 | 0 | 2026-02-11 12:59 | 2026-02-11 13:09 | 10 | 10 | Link went down and restored after 10 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
16 | NA | NA | 2026-02-11 | Salem/Amr | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-11 13:10 | 2026-02-11 13:10 | 0 | 2026-02-11 13:10 | 2026-02-11 13:18 | 8 | 8 | Link went down and restored after 8 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
17 | NA | NA | 2026-02-11 | Salem/Amr | Node Down | Link Down | Link went down | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-11 16:09 | 2026-02-11 16:09 | 0 | 2026-02-11 16:09 | 2026-02-11 16:15 | 6 | 6 | Link went down and restored after 6 mins(Auto) # It is pending from TTG | Completed | Non-maintainer | 3rd Party | TTG | Network Back Online
18 | NA | NA | 2026-02-11 | Vishnu/Amr | Node Down | Link Down | RJ45 cable was loose from switch to CCTV POE | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-11 18:31 | 2026-02-11 18:34 | 3 | 2026-02-11 19:21 | 2026-02-11 20:14 | 53 | 103 | RJ45 cable cleaned and fixed properly | Completed | Maintainer | N/a | N/a | Network Back Online
19 | NA | NA | 2026-02-12 | Vishnu/Amr | Node Down | Device Down | NA | SAL-ENC26-CE-01 |  | zone 56 | 51.2478413 25.1435454 | Outside Doha | Critical | 2026-02-12 17:16 | 2026-02-12 17:18 | 2 | 2026-02-12 17:18 | 2026-02-12 17:39 | 21 | 23 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
20 | NA | NA | 2026-02-14 | Vishnu/Amr | Node Down | Device Down | NA | SAL-ENC20-CE-01,SAL-ENC14-CE-01,SAL-ENC20-UPE-02 |  | zone 56 | 51.3063942 25.164986 | Outside Doha | Critical | 2026-02-14 16:22 | 2026-02-14 16:25 | 3 | 2026-02-14 16:25 | 2026-02-14 16:54 | 29 | 32 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
21 | Sirti-WAN-R3-Ticket-01 | NA | 2026-02-15 | Vishnu/Amr | Node Down | Device Down | FLM visited the site and found no kahramaa power in cabinet as well as FP | P028C2-ENC18-CE-01,P028C2-ENC25-CE-01,P028C2-ENC25-UPE-01 |  | Zone 18 | 25.28983, 51.51513 | Inside Doha | Critical | 2026-02-15 07:13 | 2026-02-15 07:15 | 2 | 2026-02-15 07:20 | 2026-02-15 08:48 | 88 | 95 | FLM Team contacted kharamaa and they restored the power | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
22 | Sirti-WAN-R3-Ticket-02 | NA | 2026-02-15 | Vishnu/Amr | Node Down | Device Down | FLM visited the site and found no kahramaa power in cabinet as well as FP | SAL-ENC45-CE-01 |  | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-15 07:44 | 2026-02-15 07:46 | 2 | 2026-02-15 08:31 | 2026-02-15 12:06 | 215 | 262 | Power restored by kharamaa team raised a ticket.Ref No-261100006258 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
23 | Sirti-WAN-R3-Ticket-03 | NA | 2026-02-15 | Saleem/Amr | Node Down | Link Down | FLM visited the site and found port 05 down which is connected to LAN access switch | 22FEB-ENC25-CE-01 |  | Zone 34 | 51.47088144, 25.31832397 | Inside Doha | Critical | 2026-02-15 11:38 | 2026-02-15 11:47 | 9 | 2026-02-15 11:47 | 2026-02-15 13:08 | 81 | 90 | The Alarm was cleared after LAN device came up | Completed | Maintainer | N/a | N/a | Network Back Online
24 | Sirti-WAN-R3-Ticket-04 | NA | 2026-02-16 | Amr | Node Down | Device Down | NA | P010-ENC61-CE-01,P010-ENC64-CE-01 |  | - | 51.4699752 25.1700975 | - | Critical | 2026-02-16 09:23 | 2026-02-16 09:24 | 1 | 2026-02-16 09:24 | 2026-02-16 09:40 | 16 | 17 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
25 | Sirti-WAN-R3-Ticket-05 | NA | 2026-02-17 | Vishnu/Haroon | No Power Redeundancy | Power Module Power off | MCB was tripped at SMDB | P012-ENC97-UPE-02 |  | Zone 56 | 25.1926322 51.4542203 | Outside Doha | Critical | 2026-02-17 16:37 | 2026-02-17 16:41 | 4 | 2026-02-17 17:02 | 2026-02-17 22:36 | 334 | 359 | FLM Turned on the CB and device restored | Completed | Non-maintainer | Access | Got the key from the Tunnel contractor and turned on the CB | Network Back Online
26 | Sirti-WAN-R3-Ticket-06 | NA | 2026-02-20 | Aneesh/Abubaker | Node Down | Device Down | P023C2-ENC16-CE-01 & P023C2-ENC16-UPE-02 unreachable from eSite | P023C2-ENC16-CE-01 & P023C2-ENC16-UPE-02 |  | Zone 82 | 25.228079 51.307359 | Outside Doha | Critical | 2026-02-20 04:33 | 2026-02-20 04:42 | 9 | 2026-02-20 06:50 | 2026-02-20 07:10 | 20 | 157 | FLM Turned on the CB and devices restored | Completed | Maintainer | N/a | N/a | Network Back Online
27 | Sirti-WAN-R3-Ticket-07 | NA | 2026-02-20 | Mastan/Adil | Node Down | Device Down | Port Down at CE Connected to Lan 2 Switch | SAL-ENC20-CE-01 |  | - | - | - | Critical | 2026-02-20 08:48 | 2026-02-20 09:00 | 12 | 2026-02-20 09:00 | 2026-02-20 09:04 | 4 | 16 | Device Restored(Auto) | Completed | Maintainer | N/a | N/a | Network Back Online
28 | Sirti-WAN-R3-Ticket-08 | NA | 2026-02-21 | Haroon/Masthan | Ethernet link down | Link Down | Eth link down RMC-P003 &SOC-P003 &P004-SOC PRI due QNBN activity on the link | RMC-P003 &SOC-P003 &P004-SOC PRI | - | - | - | - | Critical | 2026-02-21 12:21 | 2026-02-21 12:24 | 3 | 2026-02-21 12:24 | 2026-02-21 16:26 | 242 | 245 | Activity was finished and link was restored | Completed | Non-maintainer | 3rd Party | QNBN activity on the link | Network Back Online
29 | Sirti-WAN-R3-Ticket-09 | NA | 2026-02-22 | AMR / Vishnu | Device Down | Device Down | NA | P028C2-ENC04-CE-01-OMC LOCAL | - | - | - | - | Critical | 2026-02-22 10:32 | 2026-02-22 10:35 | 2.8333 | 2026-02-22 10:35 | 2026-02-22 10:44 | 9 | 11.8333 | Alarm Auto Cleared before flm visit the site | Completed | Maintainer | N/a | N/a | Network Back Online
30 | Sirti-WAN-R3-Ticket-10 | NA | 2026-02-22 | AMR / Erick | Link Down | Link Down | TTG team was working at RMC Datacenter on RMC-ENC-NMS-SW-01 SERVER as a part of snag clearanace | RMC-ENC-NMS-SW-01 SERVER | - | - | - | - | Critical | 2026-02-22 11:52 | 2026-02-22 11:53 | 1 | 2026-02-22 11:52 | 2026-02-22 12:03 | 11.25 | 11.25 | Alarm Auto Cleared | Completed | Non-maintainer | 3rd Party | TTG team was working at RMC Datacenter | Network Back Online
31 | Sirti-WAN-R3-Ticket-11 | NA | 2026-02-22 | AMR / Haroon / Erick | Port Module Offline | One Power Source is Down | Power cable loose between DWDM and PDU | RAA_SEC | - | Zone 28 | 25.285228, 51.551657 | Inside Doha | Critical | 2026-02-22 10:54 | 2026-02-22 10:54 | 0 | 2026-02-22 10:54 | 2026-02-22 15:24 | 269 | 269 | FLM Visit the site and found the low voltage and fix the power source | Completed | Maintainer | N/a | N/a | Network Back Online
32 | Sirti-WAN-R3-Ticket-12 | NA | 2026-02-23 | HAROON | High Temprature | LPU Board 2 | Boards Temprature higher than the upper threshold | P060-ENC18-UPE-01 | - | - | - | - | Critical | 2026-02-23 14:28 | 2026-02-23 14:30 | 2 | 2026-02-23 14:30 | 2026-02-23 14:38 | 8 | 10 | Alarm Auto Cleared before flm visit the site | Completed | Maintainer | N/a | N/a | Network Back Online
33 | Sirti-WAN-R3-Ticket-13 | NA | 2026-02-24 | Adel / Umair | Device Down | Device Down | Breaker off from the FP side | P023C3-ENC174-UPE02 & P023C3-ENC174-CE 01 | - | Zone 94 | 25.01688 51.49047 | Outside Doha | Critical | 2026-02-24 03:48 | 2026-02-24 03:52 | 5 | 2026-02-24 05:01 | 2026-02-24 05:20 | 19.5 | 92.5 | MCB was tripped , FLM switched on the MCB | Completed | Maintainer | N/a | N/a | Network Back Online
34 | Sirti-WAN-R3-Ticket-14 | NA | 2026-02-24 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | NA | DUK-ENC04-CE-01 | - | - | - | - | Critical | 2026-02-24 10:23 | 2026-02-24 10:29 | 6 | 2026-02-24 10:29 | 2026-02-24 10:46 | 16.2833 | 22.2833 | Alarm Auto Cleared | Completed | Maintainer | N/a | N/a | Network Back Online
35 | Sirti-WAN-R3-Ticket-15 | NA | 2026-02-24 | AMR | Link Down | Link Down | NA | DUK-ENC06-CE-01 | - | - | - | - | Critical | 2026-02-24 11:47 | 2026-02-24 11:47 | 0 | 2026-02-24 11:47 | 2026-02-24 12:12 | 24.7333 | 24.7333 | Alarm Auto Cleared | Completed | Maintainer | N/a | N/a | Network Back Online
36 | Sirti-WAN-R3-Ticket-16 | NA | 2026-02-24 | HAROON\Masthan | High Temprature | LPU Board 2 Heatup | Boards Temprature higher than the upper threshold | P060-ENC18-UPE-01 | - | Zone 70 | 25.388045, 51.488990 | Outside Doha | Critical | 2026-02-24 13:09 | 2026-02-24 13:10 | 1 | 2026-02-24 13:30 | 2026-02-24 15:21 | 111 | 132 | FLM Visit the site and Turn on the AC Breaker and restore the Cooling | Completed | Maintainer | N/a | N/a | Network Back Online
37 | Sirti-WAN-R3-Ticket-17 | NA | 2026-02-25 | AMR / Vishnu | Communication betweeen NMS and NE is Abnormal | Device Down / Link Down | There was no power supply in main terminals of DGME-23 | P059-C1-ENC23-CE-01 P059-C1-ENC23-UPE-02 P059-C1-ENC04-UPE-01 P059-C1-ENC42-CE-01 | - | Zone 71 | 25.451633, 51.409080 | Outside Doha | Critical | 2026-02-25 08:13 | 2026-02-25 08:14 | 1 | 2026-02-25 08:57 | 2026-02-25 10:20 | 83.25 | 127.25 | Switched the Circuit from Primary to Secondary in ATS at Feeder side(ITS FP-16) | Completed | Maintainer | N/a | N/a | Network Back Online
38 | Sirti-WAN-R3-Ticket-18 | NA | 2026-02-26 | AMR / Vishnu | Link Down | Link Down | Other Ashghal Contractor (ITS Qatar) was doing the maintenance for PTZ Camera)-On NMS port down GE1/0/15 -Huawei Switch | DUK-ENC12-CE-01 | - | Zone 80 | 25.430216, 51.149749 | Outside Doha | Critical | 2026-02-26 08:04 | 2026-02-26 08:06 | 2 | 2026-02-26 08:04 | 2026-02-26 08:42 | 37.7667 | 37.7667 | FME arrived at the site and found that ITS Qatar was performing maintenance on the PTZ camera. After the maintenance was completed, the alarm was cleared-Verified the ports in Huawei Switch, all were working well | Completed | Non-maintainer | 3rd Party | ITS Qatar was performing maintenance | Network Back Online
39 | Sirti-WAN-R3-Ticket-19 | NA | 2026-02-26 | AMR / Vishnu | Link Down | Link Down | NA -On NMS port down GE1/0/15 -Huawei Switch | SAL-ENC45-CE-01 | - | Zone 83 | 51.042739, 25.005944 | Outside Doha | Critical | 2026-02-26 08:24 | 2026-02-26 08:26 | 2 | 2026-02-26 08:26 | 2026-02-26 08:47 | 21 | 23 | FME arrived Verified the ports in Huawei Switch, all were working well- Link went down and restored after 22 min 49 sec | Completed | Maintainer | N/a | N/a | Network Back Online
40 | Sirti-WAN-R3-Ticket-20 | NA | 2026-02-26 | AMR / Vishnu | Link Down | Link Down | NA -On NMS port down GE1/0/9 -Huawei Switch | DUK-ENC16-CE-01 | - | Zone 80 | 25.432295, 51.110656 | Outside Doha | Critical | 2026-02-26 09:02 | 2026-02-26 09:04 | 2 | 2026-02-26 09:11 | 2026-02-26 09:25 | 14 | 23 | FME arrived Verified the ports in Huawei Switch, all were working well- Link went down and restored | Completed | Maintainer | N/a | N/a | Network Back Online
41 | Sirti-WAN-R3-Ticket-21 | NA | 2026-02-26 | AMR / Vishnu | Link Down | Link Down | NA -On NMS port down GE1/0/10 -Huawei Switch | SAL-ENC50-CE-01 | - | Zone 96 | 24.951308, 50.999354 | Outside Doha | Critical | 2026-02-26 10:21 | 2026-02-26 10:21 | 0 | 2026-02-26 10:29 | 2026-02-26 10:45 | 16 | 24 | FME arrived Verified the ports in Huawei Switch, all were working well- Link went down and restored | Completed | Maintainer | N/a | N/a | Network Back Online
42 | Sirti-WAN-R3-Ticket-22 | NA | 2026-02-26 | AMR / Vishnu | Communication betweeen NMS and NE is Abnormal | Communication betweeen NMS and NE is Abnormal | Issue Esclated to Imran (SALAM TECH) by call and whats app messages | P008-C3-ENC19-CE-01 P008-C3-ENC09-CE-01 P008-C3-ENC05-CE-01 P008-C3-ENC07-CE-01 P008-C3-ENC04-CE-01 P008-C3-ENC01-CE-01 | - | - | - | - | Critical | 2026-02-26 10:31 | 2026-02-26 10:31 | 0 | 2026-02-26 10:31 | 2026-02-26 11:35 | 64.1833 | 64.1833 | Issue Esclated to Imran (SALAM TECH) by call and whats app messages - All alarms got cleared | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
43 | Sirti-WAN-R3-Ticket-23 | NA | 2026-02-27 | HAROON / Patric | Heat Alarm | SFP Interface Heat Alarm | Optical Module temp too high | P010-ENC01-CE-01 | - | Zone 81 | 25.139881, 51.407393 | Outside Doha | Critical | 2026-02-27 12:08 | 2026-02-27 12:11 | 3 | 2026-02-27 12:11 | 2026-02-27 15:35 | 204 | 207 | Alarm is about SFP interface heatup overall device stats are normal, no Service Effected.alarms got cleared | Completed | Maintainer | N/a | N/a | Network Back Online
44 | Sirti-WAN-R3-Ticket-24 | NA | 2026-02-28 | AMR | Link Down | Link Down | NA | SAL-ENC67-CE-01 | - | - | - | - | Critical | 2026-02-28 11:06 | 2026-02-28 11:06 | 0 | 2026-02-28 11:06 | 2026-02-28 11:23 | 17.05 | 17.05 | Link went down and restored Auto | Completed | Maintainer | N/a | N/a | Network Back Online
45 | Sirti-WAN-R3-Ticket-25 | NA | 2026-03-03 | AMR | Link Down | Link Down | NA | DUK-ENC34-CE-01 | - | Zone 72 | 25.4537767 50.8835078 | Outside Doha | Critical | 2026-03-03 12:18 | 2026-03-03 12:18 | 0 | 2026-03-03 12:18 | 2026-03-03 12:45 | 27.05 | 27.05 | Issue esclated to RMC team and they have update Team is doing PM for End device | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
46 | Sirti-WAN-R3-Ticket-26 | NA | 2026-03-04 | AMR | PWR Module Stopped Working | Power Module Power off | PDU Was OFF | RAA-TCR-USG-02 / DWDM RAA_SEC | - | Zone 18 | 25.28522778 51.55165688 | Inside Doha | Critical | 2026-03-04 08:22 | 2026-03-04 08:24 | 2 | 2026-03-04 09:00 | 2026-03-04 09:36 | 36.7667 | 74.7667 | FLM Turned on the CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online
47 | Sirti-WAN-R3-Ticket-27 | NA | 2026-03-04 | AMR | ASH_WDM_RAA-P015-OSC_Protection ASH_WDM_RAA-P012-OSC_Protection ASH_WDM_SOC-P012-OCH-CH-54_Protection_L ASH_WDM_RMC-P012-OCH-CH-56_Protection_L ASH_WDM_SOC-P015-OCH-CH-58_Protection_S ASH_WDM_RMC-P015-OCH-CH-60_Protection_L | RAA_Sec Subrack 2 was down due to power issue | PWR cable at PDU side was loose | DWDM RAA_SEC | - | Zone 18 | 25.28522778 51.55165688 | Inside Doha | Critical | 2026-03-04 09:20 | 2026-03-04 09:20 | 0 | 2026-03-04 09:41 | 2026-03-04 09:52 | 11.7833 | 32.7833 | FLM fixed the loose power cable connection by cable tie /to be plan for PDU replacement | Completed | Maintainer | N/a | N/a | Network Back Online
48 | Sirti-WAN-R3-Ticket-28 | NA | 2026-03-08 | Abubaker | Power Module Powered off | Power Module Power off | khahromaa power shutdown | - P004-TMC-NPE-01 - P004_Pri - P004_Sec | - | - | 25.319385,51.352255 | Outside Doha | Critical | 2026-03-08 05:23 | 2026-03-08 05:28 | 5.4833 | 2026-03-08 06:01 | 2026-03-08 07:01 | 60.8333 | 98.8333 | Main Power was down due to power outage from Kharahma side, Alarms cleared after Kharahma power recovered by Kharahma team | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
49 | Sirti-WAN-R3-Ticket-29 | NA | 2026-03-08 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no PWR at ENC / FP CB was tripped | P004-ENC43-UPE-02 P004-ENC43-CE-01 P023C2-ENC43-CE-01 | - | - |  |  | Critical | 2026-03-08 17:23 | 2026-03-08 17:27 | 4 | 2026-03-08 18:02 | 2026-03-08 18:19 | 16.5 | 55.5 | The FME team reached the site and found that there was no power in the ENC cabinet. Upon checking the FP cabinet, they found that the main circuit breaker (CB) was in the OFF (tripped) state. The CB was switched ON, after which all devices were restored and the alarms were cleared | Completed | Maintainer | N/a | N/a | Network Back Online
50 | Sirti-WAN-R3-Ticket-30 | NA | 2026-03-09 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-09 08:00 | 2026-03-09 08:06 | 6.25 | 2026-03-09 09:02 | 2026-03-09 09:45 | 43.5167 | 105.5167 | there was no UPS output power , FLM Turned on the UPS | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
51 | Sirti-WAN-R3-Ticket-31 | NA | 2026-03-09 | Adel | power module stopped working , power fail | power fail | alarm is auto clear before visiting the site | P004-TMC-NPE-01 P004-sec P004-pri | - | - | 25.319385 ,51.352255 | Outside Doha | Critical | 2026-03-09 10:14 | 2026-03-09 10:17 | 3.1833 | 2026-03-09 10:17 | 2026-03-09 10:29 | 12.3333 | 15.5167 | alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
52 | Sirti-WAN-R3-Ticket-32 | NA | 2026-03-09 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-09 10:36 | 2026-03-09 10:40 | 4.2667 | 2026-03-09 11:03 | 2026-03-09 11:14 | 10.9667 | 37.9667 | there was no UPS output power , FLM Turned on the UPS | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
53 | Sirti-WAN-R3-Ticket-33 | NA | 2026-03-09 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-09 12:14 | 2026-03-09 12:18 | 4 | 2026-03-09 13:04 | 2026-03-09 13:26 | 21.9 | 71.9 | there was no UPS output power , FLM Turned on the UPS, disconnected the AC from the UPS | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
54 | Sirti-WAN-R3-Ticket-34 | NA | 2026-03-09 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | NA | P010-ENC61-CE-01 | - | - | - | - | Critical | 2026-03-09 15:38 | 2026-03-09 15:38 | 0 | 2026-03-09 15:38 | 2026-03-09 15:49 | 10.9167 | 10.9167 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
55 | Sirti-WAN-R3-Ticket-35 | NA | 2026-03-10 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | tripped CB | P029C2-ENC05-CE-01 | - | - | 25.281278° ,51.503972° | Inside Doha | Critical | 2026-03-10 07:33 | 2026-03-10 07:36 | 2.9 | 2026-03-10 08:20 | 2026-03-10 09:13 | 52.7667 | 99.7667 | FLM switched on tripped CB | Completed | Maintainer | N/a | N/a | Network Back Online
56 | Sirti-WAN-R3-Ticket-36 | NA | 2026-03-10 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | alarm is auto clear before visiting the site | SAL-ENC63-CE-01 | - | - | 24.8301249° ,50.8705931° | Outside Doha | Critical | 2026-03-10 12:15 | 2026-03-10 12:18 | 3.3167 | 2026-03-10 12:18 | 2026-03-10 13:12 | 54.3667 | 57.6833 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
57 | Sirti-WAN-R3-Ticket-37 | NA | 2026-03-11 | Aaqib | VRRP switchover performed | VRRP switchover performed | Alarm auto cleared. Suspecting link fluctuation | P023C2-Enc11-CE-01 | - | - | 25.325262° , 51.329176° | Outside Doha | Critical | 2026-11-03 04:02 | 2026-11-03 04:04 | 2.0333 | 2026-11-03 04:04 | 2026-11-03 04:06 | 2 | 4.0333 | Alarm auto cleared | Completed | Maintainer | N/a | N/a | Network Back Online
58 | Sirti-WAN-R3-Ticket-38 | NA | 2026-03-11 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Team found no output power from UPS | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-11 07:28 | 2026-03-11 07:34 | 6 | 2026-03-11 08:38 | 2026-03-11 09:50 | 71.95 | 141.95 | FLM disconnected the AC from UPS and connected it directly to CB | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
59 | Sirti-WAN-R3-Ticket-39 | NA | 2026-03-11 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | No power in cabinet | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-11 15:02 | 2026-03-11 15:05 | 3 | 2026-03-11 15:43 | 2026-03-11 16:14 | 30.6 | 71.6 | FLM disconnected the AC from UPS and connected it directly to CB , team is monitoring the UPS behavior after the action | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
60 | Sirti-WAN-R3-Ticket-40 | NA | 2026-03-12 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | DEVICE DOWN DUE TO UPS FAULTY | P010-ENC61-CE-01 | - | - | 25.1700975° ,51.4699752° | Outside Doha | Critical | 2026-03-12 09:19 | 2026-03-12 09:21 | 2 | 2026-03-12 09:57 | 2026-03-12 10:50 | 53.2667 | 91.2667 | UPS FAULTY need to replace .for now remove the UPS connetion temporary now we directly connect the device | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online
61 | Sirti-WAN-R3-Ticket-41 | NA | 2026-03-12 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | NA | SAL-ENC56-CE-01 | - | - | 24.891173, 50.938318 | - | Critical | 2026-03-12 10:52 | 2026-03-12 10:53 | 1 | 2026-03-12 10:53 | 2026-03-12 11:38 | 45.1167 | 46.1167 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online
62 | Sirti-WAN-R3-Ticket-42 | NA | 2026-03-13 | AMR | Link Down | Link Down | Cable Loose | P008C2-ENC01-CE-01 | - | - | 25.236901, 51.521726 | - | Critical | 2026-03-13 10:52 | 2026-03-13 10:57 | 5 | 2026-03-13 11:00 | 2026-03-13 11:11 | 11.6167 | 19.6167 | FME clean the cable and fix it properly | Completed | Maintainer | N/a | N/a | Network Back Online
63 | Sirti-WAN-R3-Ticket-43 | NA | 2026-03-15 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | As per Logs, there was power interruption at site | P011-Enc26-UPE-01 P011-Enc26-CE-01 | - | - | 25.22234, 51.542 | - | Critical | 2026-03-15 03:25 | 2026-03-15 03:26 | 1 | 2026-03-15 03:26 | 2026-03-15 03:31 | 5 | 6 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Devices Back Online
64 | Sirti-WAN-R3-Ticket-44 | NA | 2026-03-17 | AMR | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet | SAL-ENC14-CE-01 | - | - | 25.1858801° 51.3628538° | - | Critical | 2026-03-17 09:59 | 2026-03-17 10:01 | 2 | 2026-03-17 10:01 | 2026-03-17 10:49 | 47.2833 | 49.2833 | The Kahramaa team was working at FP. Once they completed their work and cable termination, power was restored, all devices came up, and all alarms were cleared. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
65 | Sirti-WAN-R3-Ticket-45 | NA | 2026-03-18 | Abubaker | Communication betweeen NMS and NE is Abnormal | Devices Down | As per Logs, there was power interruption at site | P006-ENC02-CE-01 | - | - | 25.2190399° 51.4369501° | - | Critical | 2026-03-18 09:59 | 2026-03-18 10:05 | 5.3167 | 2026-03-18 10:05 | 2026-03-18 10:10 | 5 | 10.3167 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
66 | Sirti-WAN-R3-Ticket-46 | NA | 2026-03-19 | Abubaker | Optical Model temperature too high | SFP Alarm | Alarm cleared automatically by itself after 1h & 11mins | P010-ENC01-CE-01 | - | - | 25.1398815, 51.4073931 | Outside Doha | Critical | 2026-03-19 14:58 | 2026-03-19 14:59 | 1.4833 | 2026-03-19 15:21 | 2026-03-19 16:09 | 48.3 | 71.7833 | Alarm auto cleared | Completed | Maintainer | N/a | N/a | Devices Back Online
67 | Sirti-WAN-R3-Ticket-47 | NA | 2026-03-20 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet due to the failure of SLFP cabient which is uder RF001 | P003-ENC10-CE-DGME-01 | - | - | 25.3735283 51.5285481 | Inside Doha | Critical | 2026-03-20 09:08 | 2026-03-20 09:12 | 3.1167 | 2026-03-20 09:31 | 2026-03-20 13:49 | 257.95 | 280.0667 | Sirti MENAA has communicated RMC to request RF001 to fix SLFP Panel, after they rectify the panel, the power back to ITS-FP and all nodes back online | Completed | Non-maintainer | 3rd Party | RF001 | Network Back Online
68 | Sirti-WAN-R3-Ticket-48 | NA | 2026-03-21 | Aaqib/Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet due to the failure of SLFP cabient which is uder RF001 | P003-Enc10-CE-DGME-01 | - | - | 25.3735283 51.5285481 | Inside Doha | Critical | 2026-03-21 07:42 | 2026-03-21 07:46 | 3.8 | 2026-03-21 08:25 | 2026-03-21 18:01 | 575.3667 | 618.8167 | Sirti MENAA has communicated RMC to request RF001 to fix SLFP Panel, after they rectify the panel, the power back to ITS-FP and all nodes back online | Completed | Non-maintainer | 3rd Party | RF001 | Network Back Online
69 | Sirti-WAN-R3-Ticket-49 | NA | 2026-03-21 | Aaqib | Link Down | Link down | Link down towards LAN | Sal-Enc45-CE-01 |  |  |  | Outside Doha | Low | 2026-03-21 12:59 | 2026-03-21 12:59 | 0 | 2026-03-21 12:59 | 2026-03-21 13:05 | 6.05 | 6.05 | Link auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
70 | Sirti-WAN-R3-Ticket-50 | NA | 2026-03-21 | Sanket | Link Down | LAN Link down | Link down towards LAN | SAL-ENC14-CE-01 |  |  |  | Outside Doha | Low | 2026-03-21 19:26 | 2026-03-21 19:26 | 0 | 2026-03-21 19:26 | 2026-03-21 19:30 | 3.9167 | 3.9167 | Link auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
71 | Sirti-WAN-R3-Ticket-51 | NA | 2026-03-21 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no power at the cabinet. | P003-ENC10-CE-DGME-01 |  |  | 25.3735283 51.5285481 | Outside Doha | Critical | 2026-03-21 20:41 | 2026-03-21 20:43 | 2 | 2026-03-21 20:52 | 2026-03-21 20:57 | 4.35 | 15.3 | Temperory generator removed and supply given from Kharamaa. | Completed | Non-maintainer | N/a | State Kahramaa | Network Back Online
72 | Sirti-WAN-R3-Ticket-52 | NA | 2026-03-21 | Sanket | Link Down | LAN Link down | Link down towards LAN | SAL-ENC20-CE-01 |  |  |  | Outside Doha | Low | 2026-03-21 20:52 | 2026-03-21 20:52 | 0 | 2026-03-21 20:53 | 2026-03-21 21:00 | 7.0833 | 8.0833 | Link auto restored. The link is down towards LAN | Completed | Maintainer | N/a | N/a | Network Back Online
73 | Sirti-WAN-R3-Ticket-53 | NA | 2026-03-21 | Sanket/Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | There was no power on the outgoing-1 of the PSU | P003-ENC37-CE-DGME-01 | - | - | 25.3364931° 51.51767° | Inside Doha | Critical | 2026-03-21 21:33 | 2026-03-21 21:36 | 3.4167 | 2026-03-21 23:00 | 2026-03-21 23:32 | 31.8 | 119.3333 | We checked outgoing-2, and it's found sufficient, we connect the switch to outgoing-2 of PSU | Completed | Maintainer | N/a | N/a | Network Back Online
74 | Sirti-WAN-R3-Ticket-54 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Device Restored before team visit | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-03-23 01:24 | 2026-03-23 01:31 | 7.25 | 2026-03-23 01:24 | 2026-03-23 05:39 | 255.1333 | 255.1333 | that switch is LAN switch managed by WAN NMS , team doesnot have the location of the switch and that escalated to 3rd party , at time 5:38 am the devices come back online without visiting | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Hichem
75 | Sirti-WAN-R3-Ticket-55 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found MCB was tripped | P017C2-ENC23-CE01 | - | - | 25.1702778° 51.4710278° | Inside Doha | Critical | 2026-03-23 02:11 | 2026-03-23 02:17 | 6.3 | 2026-03-23 04:23 | 2026-03-23 04:28 | 4.6167 | 137.0833 | FLM switched on cabinet main CB , tripped due to rain | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
76 | Sirti-WAN-R3-Ticket-56 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found no kharama power on site. | DUK-ENC30-CE01 | - | - | 25.4637854° 50.930279° | Outside Doha | Critical | 2026-03-23 02:11 | 2026-03-23 02:14 | 2.8167 | 2026-03-23 02:39 | 2026-03-23 08:53 | 374.0333 | 402.0333 | FLM visit the site and found that no kharama power on site. Ticket (Ref # 261100010894) is raised with kahrama. Device restored after kahahrama power restoration | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
77 | Sirti-WAN-R3-Ticket-57 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | cabinet main CB is off | P008C2-ENC01-CE-01 | - | - | 25.2369009° 51.521726° | Inside Doha | Critical | 2026-03-23 02:23 | 2026-03-23 02:26 | 3.4 | 2026-03-23 02:36 | 2026-03-23 04:23 | 107.8 | 120.8 | FLM switched on cabinet main CB , tripped due to rain | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
78 | Sirti-WAN-R3-Ticket-58 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Main UPS CB is tripped | P007C2-ENC82-CE-01 | - | - | 25.3045066° 51.4548113° | Inside Doha | Critical | 2026-03-23 02:39 | 2026-03-23 02:49 | 9.8667 | 2026-03-23 05:49 | 2026-03-23 05:55 | 6.5167 | 196.0833 | FLM switched on main UPS CB | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
79 | Sirti-WAN-R3-Ticket-59 | NA | 2026-03-23 | Adel | Power Module stopped working | Power Module stopped working | Team found the CB powering up Source B is faulty | P015-ENC19A-CE-01 | - | - | 25.1328013° 51.5759416° | Inside Doha | Critical | 2026-03-23 02:47 | 2026-03-23 02:52 | 4.6333 | 2026-03-23 03:12 | 2026-03-23 07:50 | 277.6833 | 302.6833 | The main CB has been replaced | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
80 | Sirti-WAN-R3-Ticket-60 | NA | 2026-03-23 | Adel | Communication betweeen NMS and NE is Abnormal | Devices Down | Team found that CB was tripped | P007C2-ENC99-UPE02 P007C2-ENC99-CE01 | - | - | 25.2967109° 51.4488814° | Inside Doha | Critical | 2026-03-23 06:17 | 2026-03-23 06:20 | 2.7667 | 2026-03-23 07:03 | 2026-03-23 07:18 | 15.4333 | 60.9333 | FLM visit the site and was found that CB was tripped. Devices restored after turning ON CB | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
81 | Sirti-WAN-R3-Ticket-61 | NA | 2026-03-23 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | CRR-ENC02-CE-01 | - | - | 25.2834083°, 51.5496912° | Inside Doha | Critical | 2026-03-23 09:09 | 2026-03-23 09:12 | 2.7333 | 2026-03-23 09:12 | 2026-03-23 09:14 | 2.35 | 5.0833 | As per log, there was khahrama interruption at site. | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
82 | Sirti-WAN-R3-Ticket-62 | NA | 2026-03-23 | Sanket | Link Down | LAN Link down | port error disable GE 1/13 | P042-ENC08-CE-01 | - | - | - | Inside Doha | Low | 2026-03-23 17:11 | 2026-03-23 17:13 | 2.3167 | 2026-03-23 17:13 | 2026-03-23 17:19 | 5.5833 | 7.9 | The port is in error disable. After shut and unshut the port link became normal. The link is down towards LAN | Completed | Maintainer | N/a | N/a | Network Back Online
83 | Sirti-WAN-R3-Ticket-63 | NA | 2026-03-23 | Sanket | Link Down | LAN Link down | The link is down towards the LAN ( D-NODE-28 is down) | DUK-ENC30-CE01 | - | - | 25°27'16.48 50°57'15.07 | Outside Doha | Medium | 2026-03-23 17:46 | 2026-03-23 17:51 | 5 | 2026-03-23 18:33 | 2026-03-23 20:51 | 138.4333 | 185.2333 | As per LAN team, D-Node 28 is down and No Kharamaa power available in the cabinet. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
84 | Sirti-WAN-R3-Ticket-64 | NA | 2026-03-23 | Sanket | Link Down | LAN Link down | Link down towards LAN | SAL-ENC32-CE-01 | - | - | 25.1165799° 51.1812367° | Outside Doha | Low | 2026-03-23 19:39 | 2026-03-23 19:41 | 2.8167 | 2026-03-23 19:41 | 2026-03-23 19:45 | 3.35 | 6.1667 | Link auto restored. The link is down towards LAN | Completed | Maintainer | N/a | N/a | Network Back Online
85 | Sirti-WAN-R3-Ticket-65 | NA | 2026-03-23 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | IE5000-2302 | - | - | - | Outside Doha | Critical | 2026-03-23 22:19 | 2026-03-23 22:21 | 2 | 2026-03-23 22:21 | 2026-03-23 22:22 | 1.2 | 3.2 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
86 | Sirti-WAN-R3-Ticket-66 | NA | 2026-03-24 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | No power in 1 phase of Khahrama | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-24 01:11 | 2026-03-24 01:17 | 5.5833 | 2026-03-24 02:06 | 2026-03-24 03:20 | 74.65 | 129 | - The node was down due to unavailability of the power in 2 phases. - Kharahma Service Request raised. - As a WA, the node connected to the phase line having power. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
87 | Sirti-WAN-R3-Ticket-67 | NA | 2026-03-24 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Team found that CB was tripped | SAL-ENC50-CE-01 | - | - | 24.9513076° 50.9993542° | Outside Doha | Critical | 2026-03-24 09:46 | 2026-03-24 09:49 | 3.2167 | 2026-03-24 09:54 | 2026-03-24 10:48 | 53.4667 | 61.85 | FLM visit the site and found MCB at FP was tripped. Device restored after switching ON MCB at FP. | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
88 | Sirti-WAN-R3-Ticket-68 | NA | 2026-03-24 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Team found that CB was tripped | P003-ENC10-CE-DGME-01 | - | - | 25.3735283 51.5285481 | Outside Doha | Critical | 2026-03-24 10:31 | 2026-03-24 10:33 | 2.0667 | 2026-03-24 11:45 | 2026-03-24 12:21 | 36.5833 | 109.9667 | FLM visit the site and found MCB at FP was tripped. Device restored after switching ON MCB at FP. | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online
89 | Sirti-WAN-R3-Ticket-69 | NA | 2026-03-24 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | Team found that CB was tripped | P007C7P1-ENC01-CE-01 | - | - | 25.339487° 51.4610983° | Inside Doha | Critical | 2026-03-24 12:04 | 2026-03-24 12:06 | 2 | 2026-03-24 12:21 | 2026-03-24 15:51 | 210.3333 | 227.3333 | As per Slam Tech team, CB was tripped. Devices restored after turning ON CB | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online
90 | Sirti-WAN-R3-Ticket-70 | NA | 2026-03-24 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | DUK-ENC06-CE-01 | - | - | 25.3954062° 51.1985851° | Outside Doha | Critical | 2026-03-24 13:38 | 2026-03-24 13:46 | 8.1667 | 2026-03-24 13:46 | 2026-03-24 13:59 | 13.0333 | 21.2 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online
91 | Sirti-WAN-R3-Ticket-71 | NA | 2026-03-25 | Abubaker | Link Down | LAN Link down | The cable toward the CCTV is disconnected (GE 1/0/10) | SAL-ENC50-CE-01 | - | - | 24.9513076, 50.9993542 | Outside Doha | Critical | 2026-03-24 23:19 | 2026-03-24 23:27 | 7.8 | 2026-03-25 00:25 | 2026-03-25 01:20 | 55.05 | 120.85 | 3rd Party ccntractor ITSQ change the RJ45 connector at POE end and Port is up | Completed | Non-maintainer | 3rd Party | 3rd Party ccntractor | Port is up and alarm cleared | Khadar basha syed
92 | Sirti-WAN-R3-Ticket-72 | NA | 2026-03-25 | Abubaker | Link Down | LAN Link down | RJ45 Connector was found faulty | SAL-ENC50-CE-01 | - | - | 24.9513076, 50.9993542 | Outside Doha | Critical | 2026-03-25 02:42 | 2026-03-25 02:48 | 5.8833 | 2026-03-25 02:48 | 2026-03-25 03:01 | 12.6667 | 18.55 | Auto clear before team visit | Completed | Maintainer | N/a | N/a | Port is up and alarm cleared
93 | Sirti-WAN-R3-Ticket-73 | NA | 2026-03-25 | Abubaker | Link Down | LAN Link down | Short Circuit in 3 Phase khahrama connection | DUK-ENC12-CE-01 | - | - | 25.4322949° 51.1106559° | Outside Doha | Critical | 2026-03-25 03:53 | 2026-03-25 03:56 | 2.9667 | 2026-03-25 04:46 | 2026-03-25 06:24 | 97.3667 | 150.3167 | The cabinet power issue was caused by a short circuit between R/Y/B phases and Neutral in the power cable of Khahrama | Completed | Maintainer | N/a | N/a | Network Back Online | Umair Rahman
94 | Sirti-WAN-R3-Ticket-74 | NA | 2026-03-25 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | CB was found faulty | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-25 08:20 | 2026-03-25 08:24 | 4.4667 | 2026-03-25 09:01 | 2026-03-25 10:00 | 58.7833 | 100.6333 | Device was down due to faulty CB. Team change CB connection with spare CB and device restored | Completed | Maintainer | N/a | N/a | Network Back Online | Kwadwo Ofosu
95 | Sirti-WAN-R3-Ticket-75 | NA | 2026-03-25 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | During PPM activity / AC compressor faulty when the team make AC CB ON - the main CB went OFF | P029C2-ENC05-CE-01 | - | - | 25.281278 51.503972 | Inside Doha | Critical | 2026-03-25 12:50 | 2026-03-25 12:51 | 1 | 2026-03-25 12:54 | 2026-03-25 12:57 | 2.1 | 6.1 | During PPM activity / AC compressor faulty when the team make AC CB ON - the main CB went OFF /team make CB ON and all alarms got cleared | Completed | Maintainer | N/a | N/a | Network Back Online | Hecham
96 | Sirti-WAN-R3-Ticket-76 | NA | 2026-03-25 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | P059C1-N2-ENC19-CE-01 | - | - | 25.43425476° 51.412436° | Inside Doha | Critical | 2026-03-25 14:18 | 2026-03-25 14:22 | 4.45 | 2026-03-25 14:22 | 2026-03-25 14:24 | 2 | 6.45 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
97 | Sirti-WAN-R3-Ticket-77 | NA | 2026-03-26 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Device Restored before team visit | IE5000-1003.ashghal | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-03-26 06:36 | 2026-03-26 06:41 | 4.6333 | 2026-03-26 06:41 | 2026-03-26 06:58 | 16.5333 | 21.1667 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
98 | Sirti-WAN-R3-Ticket-78 | NA | 2026-03-26 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | QBC team is working at FP | SAL-ENC20-CE-01 SAL-ENC20-UPE-02 | - | - | 25.164986° 51.3063942 | Inside Doha | Critical | 2026-03-26 11:06 | 2026-03-26 11:09 | 3.1 | 2026-03-26 11:09 | 2026-03-26 11:36 | 26.8833 | 29.9833 | QBC team is working at Fidder Piller | Completed | Non-maintainer | 3rd Party | 3rd Party ccntractor | Network Back Online | Patric
99 | Sirti-WAN-R3-Ticket-79 | NA | 2026-03-26 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Sub Main CB breaker tripping along with AC CB Due to AC Defect | IE5000-1003.ashghal | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-03-26 10:15 | 2026-03-26 10:20 | 4.7333 | 2026-03-26 10:55 | 2026-03-26 11:08 | 13.05 | 52.7833 | Sub Main CB breaker Restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Hichem
100 | Sirti-WAN-R3-Ticket-80 | NA | 2026-03-26 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Sub Main CB breaker tripping along with AC CB due to AC defect during PPM | IE5000-1003.ashghal | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-03-26 12:34 | 2026-03-26 12:38 | 4 | 2026-03-26 12:38 | 2026-03-26 12:48 | 10.5 | 14.5 | Change AC Capacitor and deep cleaning of all AC components | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Hichem
101 | Sirti-WAN-R3-Ticket-81 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | alarm is auto clear before visiting the site | SAL-ENC26-CE-01 | - | - | 25.1435454° 51.2478413° | Outside Doha | Critical | 2026-03-26 17:14 | 2026-03-26 17:16 | 1.7167 | 2026-03-26 17:14 | 2026-03-26 17:17 | 2.25 | 2.25 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online | -
102 | Sirti-WAN-R3-Ticket-82 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | FLM found no power inside cabinet | DUK-ENC24-CE-01 | - | - | 25.435778° 51.0066732° | Outside Doha | Critical | 2026-03-26 16:38 | 2026-03-26 16:40 | 1.9 | 2026-03-26 17:54 | 2026-03-26 18:19 | 24.8833 | 100.7833 | FLM switched on main CB that was tripped | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | sanjeewa
103 | Sirti-WAN-R3-Ticket-83 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | No Khahroma power at cabenit | DUK-ENC20-CE-01 | - | - | 25.427405° 51.0546006° | Outside Doha | Critical | 2026-03-26 17:46 | 2026-03-26 17:49 | 2.6333 | 2026-03-26 19:33 | 2026-03-26 23:19 | 226.3667 | 333 | Esclated to Kharahma & power was restored, all devices came up | Completed | Non-maintainer | Environmental & 3rd Party | Rain Event & State Kahramaa | Network Back Online | sanjeewa
104 | Sirti-WAN-R3-Ticket-84 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | main Cabinet CB was tripped | P060-ENC18-CE-GME-01 | - | - | 25.4042479° 51.4923233° | Outside Doha | Critical | 2026-03-26 17:35 | 2026-03-26 17:40 | 4.5667 | 2026-03-26 20:02 | 2026-03-26 20:16 | 13.85 | 160.4167 | FLM switched on main CB that was tripped | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | najeeb
105 | Sirti-WAN-R3-Ticket-85 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power at cabinet | SAL-ENC50-CE-01 | - | - | 24.9513076° 50.9993542° | Outside Doha | Critical | 2026-03-26 18:17 | 2026-03-26 18:18 | 1.2167 | 2026-03-26 20:49 | 2026-03-26 21:15 | 26.4667 | 178.6833 | FLM switched on main CB at feeder pillar | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | hassan
106 | Sirti-WAN-R3-Ticket-86 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power inside cabinet | SAL-ENC45-CE-01 | - | - | 25.005944° 51.042739° | Outside Doha | Critical | 2026-03-26 18:20 | 2026-03-26 18:21 | 1.2833 | 2026-03-26 19:35 | 2026-03-26 20:04 | 28.7 | 103.9833 | FLM switched on main CB at feeder pillar | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | hassan
107 | Sirti-WAN-R3-Ticket-87 | NA | 2026-03-26 | Adel | Link Down | LAN device down | No Kharahma Power at the LAN device | SAL-ENC67-CE-01 | - | - | 24.7761642° 50.8665552° | Outside Doha | Critical | 2026-03-26 18:28 | 2026-03-26 18:37 | 9.0167 | 2026-03-26 19:39 | 2026-03-26 23:44 | 245.0833 | 316.1 | Esclated to Kharahma & power was restored, all devices came up | Completed | Non-maintainer | Environmental & 3rd Party | Rain Event & State Kahramaa | Network Back Online | hassan
108 | Sirti-WAN-R3-Ticket-88 | NA | 2026-03-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power inside cabinet | P029C1-ENC02-CE-01 | - | - | 25.2779777° 51.4661648 | Inside Doha | Critical | 2026-03-26 18:48 | 2026-03-26 18:53 | 4.55 | 2026-03-26 21:31 | 2026-03-26 22:07 | 35.7 | 198.25 | FLM switched on main CB at feeder pillar & bypass the UPS as it is tripping the FB CB | Completed | Non-maintainer | Environmental | Rain Event | Network Back Online | aneesh
109 | Sirti-WAN-R3-Ticket-89 | NA | 2026-03-26 | Adel | Farwarding Engine fail | Device hardware fault | No abonormalities found at site | SAL-ENC32-CE-01 | - | - | 25.1165799° 51.1812367° | Outside Doha | Critical | 2026-03-26 22:15 | 2026-03-26 22:25 | 9.55 | 2026-03-26 22:18 | 2026-03-27 00:15 | 116.6667 | 119.2167 | Performed a hardware reboot for the device | Completed | Non-maintainer | Environmental | Rain Event | Alarm Cleared | aneesh
110 | Sirti-WAN-R3-Ticket-90 | NA | 2026-03-28 | Aaqib | Link Down | 1x10G Link Down | port was in Err-Disabled status | P028C2-Enc06-DGME-CE-01 port TE 1/25 | - | - | 25.2892675° 51.5213447° | Inside Doha | Critical | 2026-03-28 23:35 | 2026-03-28 23:39 | 3.4667 | 2026-03-28 23:39 | 2026-03-28 23:39 | 0 | 3.4667 | Issue resolved after shut/unshut port | Completed | Maintainer | N/a | N/a | Alarm Cleared | -
111 | Sirti-WAN-R3-Ticket-91 | NA | 2026-03-28 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | IE5000-3202 | - | - |  | Inside Doha | Critical | 2026-03-29 01:45 | 2026-03-29 01:48 | 2.65 | 2026-03-29 01:48 | 2026-03-29 01:49 | 0.58333 | 3.2333 | As per Logs, there was power interruption at schema site Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
112 | Sirti-WAN-R3-Ticket-92 | NA | 2026-03-28 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | DC23-Enc101-CE-01 | - | - | 25.3204° 51.470367° | Inside Doha | Critical | 2026-03-29 01:45 | 2026-03-29 01:47 | 2.1 | 2026-03-29 01:47 | 2026-03-29 01:51 | 3.8167 | 5.9167 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
113 | Sirti-WAN-R3-Ticket-93 | NA | 2026-03-28 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | DC23-Enc102-CE-01 | - | - | 25.321261° 51.473693° | Inside Doha | Critical | 2026-03-29 01:45 | 2026-03-29 01:47 | 2.1 | 2026-03-29 01:47 | 2026-03-29 01:51 | 3.8167 | 5.9167 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
114 | Sirti-WAN-R3-Ticket-94 | NA | 2026-03-28 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | DC23-Enc104-CE-01 | - | - | 25.320812° 51.469483° | Inside Doha | Critical | 2026-03-29 01:45 | 2026-03-29 01:47 | 2.1 | 2026-03-29 01:47 | 2026-03-29 01:51 | 3.8167 | 5.9167 | As per Logs, there was power interruption at site. Device auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
115 | Sirti-WAN-R3-Ticket-95 | NA | 2026-03-29 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | IE5000-1003.ashghal | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-03-29 09:25 | 2026-03-29 09:29 | 3.95 | 2026-03-29 09:29 | 2026-03-29 09:40 | 11 | 14.95 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Hichem
116 | Sirti-WAN-R3-Ticket-96 | NA | 2026-03-29 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-29 09:40 | 2026-03-29 09:41 | 1.4833 | 2026-03-29 09:41 | 2026-03-29 09:42 | 0.71667 | 2.2 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
117 | Sirti-WAN-R3-Ticket-97 | NA | 2026-03-29 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-29 09:44 | 2026-03-29 09:45 | 0.96667 | 2026-03-29 09:45 | 2026-03-29 09:47 | 2.0167 | 2.9833 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
118 | Sirti-WAN-R3-Ticket-98 | NA | 2026-03-29 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | SAL-ENC50-CE-01 | - | - | 24.9513076° 50.9993542° | Outside Doha | Critical | 2026-03-29 10:51 | 2026-03-29 10:53 | 2.3333 | 2026-03-29 10:53 | 2026-03-29 10:53 | 0.25 | 2.5833 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
119 | Sirti-WAN-R3-Ticket-99 | NA | 2026-03-29 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Khahrama Outage | SAL-ENC50-CE-01 | - | - | 24.9513076° 50.9993542° | Outside Doha | Critical | 2026-03-29 13:41 | 2026-03-29 13:43 | 2.05 | 2026-03-29 13:43 | 2026-03-29 13:43 | 0.33333 | 2.3833 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
120 | Sirti-WAN-R3-Ticket-100 | NA | 2026-03-29 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | FLM found that Another contractor(prime craft) is working on the feeder pillar | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-29 13:33 | 2026-03-29 13:37 | 4 | 2026-03-29 13:37 | 2026-03-29 14:22 | 44.6833 | 48.6833 | FLM found that Another contractor(prime craft) is working on the feeder pillar | Completed | Non-maintainer | 3rd Party | Work carried out by another subcontractor | Network Back Online | Irshad
121 | Sirti-WAN-R3-Ticket-101 | NA | 2026-03-29 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | FLM found that Another contractor(prime craft) is working on the feeder pillar | SAL-ENC50-CE-01 | - | - | 24.9513076° 50.9993542° | Outside Doha | Critical | 2026-03-29 15:57 | 2026-03-29 15:59 | 2.3833 | 2026-03-29 15:59 | 2026-03-29 16:38 | 38.7 | 41.0833 | FLM found that Another contractor(prime craft) is working on the feeder pillar | Completed | Non-maintainer | 3rd Party | Work carried out by another subcontractor | Network Back Online | Masthanbasha
122 | Sirti-WAN-R3-Ticket-102 | NA | 2026-03-29 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-29 17:42 | 2026-03-29 17:44 | 1.7667 | 2026-03-29 17:44 | 2026-03-29 17:44 | 0.21667 | 1.9833 | As per Logs, there was power interruption at site. Device auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
123 | Sirti-WAN-R3-Ticket-103 | NA | 2026-03-29 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | FLM found that the CB inside the feeder pillar is tripped | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-29 19:34 | 2026-03-29 19:43 | 9.45 | 2026-03-29 20:41 | 2026-03-29 21:24 | 43.05 | 110.5 | FLM switched on main CB at feeder pillar. Breaker tripped due to Kahramaa instability | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Masthanbasha
124 | Sirti-WAN-R3-Ticket-104 | NA | 2026-03-30 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | AC FAN faulty (Overheating) | SAL-ENC09-CE-01 | - | Zone 55 | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-30 06:57 | 2026-03-30 06:58 | 1.1667 | 2026-03-30 06:58 | 2026-03-30 06:59 | 0.85 | 2.0167 | The alarm auto restored however the FLM went to the site and replaced the fan compressor | Completed | Maintainer | N/a | N/a | Network Back Online | -
125 | Sirti-WAN-R3-Ticket-105 | NA | 2026-03-30 | Sanket | Optical Invalid | High power | High power in 100GE 1/4/0/33 | RMC-ENC-SSW-01 | - | - |  | Inside Doha | Low | 2026-03-30 08:40 | 2026-03-30 08:45 | 5.5 | 2026-03-30 08:52 | 2026-03-30 09:20 | 28.3333 | 40.3333 | 5dB attenuator added in both the port of RMC-ENC-SSW-01 (100GE 1/4/0/33 and 100GE 2/4/0/33) | Completed | Maintainer | N/a | N/a | Network Back Online | Arfa
126 | Sirti-WAN-R3-Ticket-106 | NA | 2026-03-30 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Khahram power line cut | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-30 17:58 | 2026-03-30 18:03 | 4.7 | 2026-03-30 19:02 | 2026-03-31 01:21 | 379.1667 | 442.8667 | Khahram power line issue.khahram team is working on finding fault at power lines. Site was temporery powered up with PG. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Sanjeewa / Ghulam
127 | Sirti-WAN-R3-Ticket-107 | NA | 2026-03-30 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | MCB at FP was tripped. | P007C2-ENC89-CE-01 P007C2-ENC89-CE-02 | - | Zone 52 | 25.2960119° 51.4742727° | Inside Doha | Critical | 2026-03-30 20:58 | 2026-03-30 21:07 | 9.1167 | 2026-03-30 21:36 | 2026-03-30 23:26 | 109.65 | 147.7667 | MCB was tripped at FP. PG was installed during finding FP location. | Completed | Maintainer | N/a | N/a | Network Back Online | Masthanbasha
128 | Sirti-WAN-R3-Ticket-108 | NA | 2026-03-31 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | alarm is auto clear before visiting the site | IE5000-1003.ashghal | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-03-31 11:26 | 2026-03-31 11:28 | 2.2333 | 2026-03-31 11:28 | 2026-03-31 11:38 | 10.4333 | 12.6667 | alarm is auto clear before visiting the site , suspecting power is flapped | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
129 | Sirti-WAN-R3-Ticket-109 | NA | 2026-03-31 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | MCB at FP was tripped. | P007C2-ENC89-CE-01 P007C2-ENC89-CE-02 | - | Zone 52 | 25.2960119° 51.4742727° | Inside Doha | Critical | 2026-03-31 14:00 | 2026-03-31 14:06 | 6.4167 | 2026-03-31 14:51 | 2026-03-31 15:29 | 38 | 89.4167 | MCB was tripped at FP, FLM switch on the MCB at the FP | Completed | Maintainer | N/a | N/a | Network Back Online | Khadar basha syed
130 | Sirti-WAN-R3-Ticket-110 | NA | 2026-03-31 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Device was energized by generator | SAL-ENC09-CE-01 | - | - | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-03-31 19:11 | 2026-03-31 19:13 | 2.4 | 2026-03-31 19:13 | 2026-03-31 19:20 | 7.0833 | 9.4833 | FLM disconneced the Generator and powered up the device through Kharahma supply | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Sanjeewa
131 | Sirti-WAN-R3-Ticket-111 | NA | 2026-04-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | UPS CB is tripped when Aircondition is on | P028C2-ENC04-CE-01.omc.local |  |  | 25.2791625° 51.5290008° | Inside Doha | Critical | 2026-04-01 09:10 | 2026-04-01 09:12 | 2.5 | 2026-04-01 09:12 | 2026-04-01 09:21 | 9.4833 | 11.9833 | Device auto restored however the FLM went to the site and switched on the UPS CB and switched off the Aircondition. | Completed | Maintainer | N/a | N/a | Network Back Online | hicham
132 | Sirti-WAN-R3-Ticket-112 | NA | 2026-04-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team | P008C3-ENC01-CE-01 |  |  | 25.2614822° 51.4801647° | Inside Doha | Critical | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 | According to Mr. Salman from Salam Tech, there was DC power issue in the switch at LAN Ring which was resolved after restarting switch . The fluctuation had been occurring repeatedly at intervals of 2, 4, and 5 minutes during the mentioned time frame | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
133 | Sirti-WAN-R3-Ticket-113 | NA | 2026-04-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team | P008C3-ENC04-CE-01 |  |  | 25.2570167° 51.4842069° | Inside Doha | Critical | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
134 | Sirti-WAN-R3-Ticket-114 | NA | 2026-04-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team | P008C3-ENC07-CE-01 |  |  | 25.2503634° 51.4854925° | Inside Doha | Critical | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
135 | Sirti-WAN-R3-Ticket-115 | NA | 2026-04-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team | P008C3-ENC05-CE-01 |  |  | 25.2565555° 51.4854834° | Inside Doha | Critical | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
136 | Sirti-WAN-R3-Ticket-116 | NA | 2026-04-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team | P008C3-ENC09-CE-01 |  |  | 25.253746° 51.4904411° | Inside Doha | Critical | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
137 | Sirti-WAN-R3-Ticket-117 | NA | 2026-04-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team | P008C3-ENC19-CE-01 |  |  | 25.2366977° 51.4964187° | Inside Doha | Critical | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
138 | Sirti-WAN-R3-Ticket-118 | NA | 2026-04-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | DC Power Issue in ring switch as per Salam tech team | P008C3-ENC25-CE-01 |  |  | 25.2341068° 51.50261° | Inside Doha | Critical | 2026-04-01 23:21 | 2026-04-01 23:28 | 6.3667 | 2026-04-01 23:28 | 2026-04-01 23:48 | 19.65 | 26.0167 |  | Completed | Non-maintainer | Defect | DC power issue | Network Back Online | -
139 | Sirti-WAN-R3-Ticket-119 | NA | 2026-04-02 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | P059C1-Enc42-CE-01 |  |  | 25.56931971° 51.41540451° | Outside Doha | Critical | 2026-04-02 02:51 | 2026-04-02 02:55 | 4 | 2026-04-02 02:55 | 2026-04-02 02:56 | 1 | 5 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
140 | Sirti-WAN-R3-Ticket-120 | NA | 2026-04-02 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-02 06:38 | 2026-04-02 06:44 | 6 | 2026-04-02 06:44 | 2026-04-02 06:58 | 14 | 20 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
141 | Sirti-WAN-R3-Ticket-121 | NA | 2026-04-02 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no power at cabinet | P028C2-ENC01-CE-01.omc.local |  |  | 25.283910° 51.5496128° | Inside Doha | Critical | 2026-04-02 09:14 | 2026-04-02 09:18 | 4.4833 | 2026-04-02 09:27 | 2026-04-02 09:35 | 7.9333 | 21.4167 | FLM switched on tripped CB at FP | Completed | Maintainer | N/a | N/a | Network Back Online | Hicham
142 | Sirti-WAN-R3-Ticket-122 | NA | 2026-04-02 | AMR | Power Fault | Power Fault | UPS Battery Faulty | SAL-ENC20-CE-01 |  |  | 51.3063942 25.164986 | Inside Doha | Low | 2025-09-11 16:10 | 2025-09-11 16:11 | 1 | 2026-04-02 12:27 | 2026-04-02 12:59 | 32 | 292129.15 | Action: UPS restarted. Now All power modules are running stable. UPS output : 246V | Completed | Non-maintainer | N/a | TTG | Network Back Online | Hicham
143 | Sirti-WAN-R3-Ticket-123 | NA | 2026-04-02 | AMR | Poower Modules Stopped Working | Poower Modules Stopped Working | UPS Battery Faulty | SAL-ENC20-CE-01 |  |  | 51.3063942 25.164986 | Inside Doha | Critical | 2026-03-31 17:23 | 2026-03-31 17:24 | 0.93333 | 2026-04-02 12:27 | 2026-04-02 12:59 | 32 | 2615.9333 | Action: UPS restarted. Now All power modules are running stable. UPS output : 246V | Completed | Non-maintainer | N/a | TTG | Network Back Online | Hicham
144 | Sirti-WAN-R3-Ticket-124 | NA | 2026-04-03 | Sanket | Communication betweeen NMS and NE is Abnormal | Devices Fluctuation | Alarm is auto clear before visiting the site. The devices was fluctuated for 20 seconds in the interval of seven. The Schema maitained by Salam Tech | P014-ENC04-DSW04 |  |  | 25.254° 51.52375° | Inside Doha | Critical | 2026-04-03 02:22 | 2026-04-03 02:27 | 5 | 2026-04-03 02:27 | 2026-04-03 03:11 | 44.2167 | 49.2167 | Alarm is auto clear before visiting the site. The devices was fluctuated for 20 seconds in the interval of seven. The Schema maitained by Salam Tech | Completed | Non-maintainer | 3rd Party | Salam Tech | Network Back Online | -
[8 empty] | P014-ENC07-DSW07 |  |  | 25.2546112° 51.5246112° | Inside Doha | Critical | 2026-04-03 02:21 | 2026-04-03 02:27 | 5.6833 | 2026-04-03 02:27 | 2026-04-03 03:07 | 40.2167 | 45.9
[8 empty] | P014-ENC10-DSW10 |  |  | 25.253896 51.535995 | Inside Doha | Critical | 2026-04-03 02:27 | 2026-04-03 02:32 | 5.0667 | 2026-04-03 02:32 | 2026-04-03 03:06 | 34.2 | 39.2667
[8 empty] | P014-ENC11-DSW11 |  |  | 25.2545833° 51.5367222° | Inside Doha | Critical | 2026-04-03 02:38 | 2026-04-03 02:40 | 1.5833 | 2026-04-03 02:40 | 2026-04-03 03:06 | 26.3833 | 27.9667
[8 empty] | P014-ENC12-DSW12 |  |  | 25.524911 51.54895 | Inside Doha | Critical | 2026-04-03 02:33 | 2026-04-03 02:40 | 7.25 | 2026-04-03 02:40 | 2026-04-03 03:06 | 26.3833 | 33.6333
145 | Sirti-WAN-R3-Ticket-125 | NA | 2026-04-03 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | P015-ENC93-CE-01 |  |  | 25.1143801° 51.5957564° | Inside Doha | Critical | 2026-04-03 08:47 | 2026-04-03 08:49 | 2 | 2026-04-03 08:49 | 2026-04-03 08:49 | 0.56667 | 2.5667 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | -
146 | Sirti-WAN-R3-Ticket-126 | NA | 2026-04-04 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | P040-CPE02-ENC21-DSW |  |  | 25.189354 51.448508 | Inside Doha | Critical | 2026-04-04 11:10 | 2026-04-04 11:20 | 10.0333 | 2026-04-04 11:24 | 2026-04-04 11:32 | 7.95 | 21.9833 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Maintainer | N/a | N/a | Network Back Online | Rizwan
147 | Sirti-WAN-R3-Ticket-127 | NA | 2026-04-05 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma power fluctuation | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-05 14:32 | 2026-04-05 14:37 | 5.4 | 2026-04-05 14:32 | 2026-04-05 14:41 | 9.6333 | 9.6333 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
148 | Sirti-WAN-R3-Ticket-128 | NA | 2026-04-05 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma power fluctuation | P008C2-Enc24-CE-01 |  |  | 25.2504372° 51.5239383° | Inside Doha | Critical | 2026-04-05 16:18 | 2026-04-05 16:20 | 1.8667 | 2026-04-05 16:20 | 2026-04-05 16:23 | 3.2167 | 5.0833 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
149 | Sirti-WAN-R3-Ticket-129 | NA | 2026-04-05 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | CB tripped during PPM | P008C2-Enc24-CE-01 |  |  | 25.2504372° 51.5239383° | Inside Doha | Critical | 2026-04-05 17:09 | 2026-04-05 17:12 | 3.4167 | 2026-04-05 17:12 | 2026-04-05 17:14 | 1.8667 | 5.2833 | Device went down due to ongoing PPM activity by FLM | Completed | Non-maintainer | Scheduled Works | PPM | Network Back Online | -
150 | Sirti-WAN-R3-Ticket-130 | NA | 2026-04-06 | Sanket/Abu baker | Communication betweeen NMS and NE is Abnormal | Device Down | Power was OK at site while device is down | IE5000-3903 |  |  | 25.263350 51.496886 | Inside Doha | Critical | 2026-04-06 05:43 | 2026-04-06 05:53 | 9.7333 | 2026-04-06 06:33 | 2026-04-06 07:21 | 47.9167 | 97.65 | Device restored after changing the power from PS1 to PS2 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Hicham
151 | Sirti-WAN-R3-Ticket-131 | NA | 2026-04-07 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Alarm is auto cleared before FLM visiting the site. As per logs it is related to power instability. IE5000-1702, IE5000-3101 & IE5000-6009 was flapped for around 40 Sec (Ring conversion time) | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-07 07:44 | 2026-04-07 07:48 | 3.6167 | 2026-04-07 07:44 | 2026-04-07 07:50 | 6 | 6 | Device Auto restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
152 | Sirti-WAN-R3-Ticket-132 | NA | 2026-04-07 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma power fluctuation | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-07 09:47 | 2026-04-07 09:50 | 2.5833 | 2026-04-07 09:47 | 2026-04-07 09:56 | 8.6667 | 8.6667 | FLM team was on site during incident, observed power interruption caused the device to be down | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Najeeb
153 | Sirti-WAN-R3-Ticket-133 | NA | 2026-04-08 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-08 05:40 | 2026-04-08 05:43 | 3 | 2026-04-08 06:29 | 2026-04-08 07:49 | 79.8167 | 128.7333 | Device was down due to power outage | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Kwadwo
154 | Sirti-WAN-R3-Ticket-134 | NA | 2026-04-08 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-08 08:06 | 2026-04-08 08:09 | 2.5333 | 2026-04-08 08:06 | 2026-04-08 08:56 | 49.6833 | 49.6833 | Device was down due to power outage | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online
155 | Sirti-WAN-R3-Ticket-135 | NA | 2026-04-08 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | P015-ENC22B-UPE-02 P015-ENC24A-CE-01 P015-SS1-USG-02 P015-ENC19A-CE-01 P015-ENC80A-CE-01 P015-SS1-CE-01 P015-ENC18-CE-01 P015-ENC22A-CE-01 P015-ENC22B-CE-01 P015-ENC56-CE-01 P015-ENC93-CE-01 P015-SS1-USG-01 | - | Zone 90 | 25.131934° 51.5866756° | Inside Doha | Critical | 2026-04-08 07:11 | 2026-04-08 07:22 | 10.8333 | 2026-04-08 08:10 | 2026-04-08 13:51 | 341.3167 | 400.15 | Devices were down due to Kharahma major outage in multiple sites which affected multiple nodes as well as the ring protection There was no Kharahma power at the following: P015-ENC22B-UPE-02 P015-ENC24A-CE-01 P015-ENC19A-CE-01 P015-ENC18-CE-01 P015-ENC22A-CE-01 P015-ENC22B-CE-01 P015-ENC56-CE-01 | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Najeeb / Hicham
156 | Sirti-WAN-R3-Ticket-136 | NA | 2026-04-09 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-09 06:21 | 2026-04-09 06:23 | 1.65 | 2026-04-09 06:57 | 2026-04-09 07:28 | 31.5667 | 67.1 | Device was down due to KHARAMAA issue. Temporary genertaor is connected to resolved the issue. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Irshad
157 | Sirti-WAN-R3-Ticket-137 | NA | 2026-04-09 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-09 12:08 | 2026-04-09 12:12 | 3.35 | 2026-04-09 12:18 | 2026-04-09 12:26 | 7.35 | 17.35 | Due to Kharahma power, the device was running on generator.Suddenly the circuit breaker tripped and the device shut down. Later, the circuit breaker was turned ON again. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Irshad
158 | Sirti-WAN-R3-Ticket-138 | NA | 2026-04-09 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-09 13:00 | 2026-04-09 13:04 | 4 | 2026-04-09 13:10 | 2026-04-09 13:16 | 5.7167 | 15.7167 | We removed the generator and started the device on Kahramaa | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Irshad
159 | Sirti-WAN-R3-Ticket-139 | NA | 2026-04-09 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | device down flapped for 5 min and auto-restored | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-09 16:11 | 2026-04-09 16:13 | 2 | 2026-04-09 16:11 | 2026-04-09 16:16 | 5 | 5 | device down flapped for 5 min and auto-restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
160 | Sirti-WAN-R3-Ticket-140 | NA | 2026-04-10 | Abubaker | Link Down (100GE 1/0/1) | 100GE Link Down | Link Down (100GE 1/0/1) due to QNBN Planned Activity | P023C1-ENC01-UPE-01 | - |  | 25.111748° 51.583897° | outside Doha | Critical | 2026-04-10 01:01 | 2026-04-10 01:06 | 5 | 2026-04-10 01:18 | 2026-04-10 03:20 | 122 | 139 | Planned activity by QNBN (Ref # PWA-RMD-0104) | Completed | Non-maintainer | 3rd Party | QNBN | Link is up and alarm cleared | -
161 | Sirti-WAN-R3-Ticket-141 | NA | 2026-04-10 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Traffic Signal Contractor Activity | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-10 04:26 | 2026-04-10 04:34 | 8 | 2026-04-10 04:34 | 2026-04-10 04:51 | 17 | 25 | Device went down due to TS contractor activity, the switched off the CB. | Completed | Non-maintainer | 3rd Party | TS contractor | Network Back Online | Ghulam
162 | Sirti-WAN-R3-Ticket-142 | NA | 2026-04-10 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KTC team turned off Breaker at FP for their activity | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-10 07:15 | 2026-04-10 07:18 | 3 | 2026-04-10 07:18 | 2026-04-10 07:24 | 6 | 9 | Device went down due to TS contractor activity, the switched off the CB. | Completed | Non-maintainer | 3rd Party | TS contractor | Network Back Online | Ghulam
163 | Sirti-WAN-R3-Ticket-143 | NA | 2026-04-10 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Traffic Signal Contractoris working | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-10 19:40 | 2026-04-10 19:42 | 2 | 2026-04-10 19:42 | 2026-04-10 20:40 | 58 | 60 | No power in the cabinet. Tripped off main ITS-FP- breaker | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Eric
164 | Sirti-WAN-R3-Ticket-144 | NA | 2026-04-11 | Aaqib | Communication betweeen NMS and NE is Abnormal | Devices Down | Kharahma Outage | P059C1-Enc04-UPE-01 P059C1-Enc04-CE-01 |  | Zone 70 | 25.3653937° 51.4467471° | Outside Doha | Critical | 2026-04-11 08:47 | 2026-04-11 08:50 | 3.1333 | 2026-04-11 10:09 | 2026-04-11 10:50 | 40.85 | 123.3333 | Khahrama outage. Device was temoprery powered up with DG . Later discnnected on khahrama restoration | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | Rizwan
165 | Sirti-WAN-R3-Ticket-145 | NA | 2026-04-12 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. | RAA-ENC24-UPE-02 RAA-ENC24-CE-01 | - |  | 25.23647° 51.58650° | Inside Doha | Critical | 2026-04-12 03:17 | 2026-04-12 03:20 | 3.4167 | 2026-04-12 03:17 | 2026-04-12 03:57 | 40.35 | 40.35 | As per the logs indicating a power interruption.Devices auto Restored before FLM reached the site. | Completed | Maintainer | N/a | N/a | Network Back Online | Ghulam / SARJOON
166 | Sirti-WAN-R3-Ticket-146 | NA | 2026-04-12 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | CB tripped at FP end | P002-ENC13-CE-01 |  |  | 25.248 51.47325 | Inside Doha | Critical | 2026-04-12 07:24 | 2026-04-12 07:28 | 4.3333 | 2026-04-12 08:08 | 2026-04-12 08:37 | 29.35 | 73.2 | CB tripped at FP side. Site restored after turning on CB | Completed | Maintainer | N/a | N/a | Network Back Online | Rizwan
167 | Sirti-WAN-R3-Ticket-147 | NA | 2026-04-12 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | 3rd party team was working at FP for their activity | RAA-Enc24-UPE-01 RAA-Enc24-CE-01 |  |  | 25.23647° 51.58650° | Inside Doha | Critical | 2026-04-12 09:49 | 2026-04-12 09:54 | 4.55 | 2026-04-12 09:54 | 2026-04-12 10:07 | 13.1167 | 17.6667 | Upon FLM arrival, team found 3rd party contractor was working at FP. Device restored after khahrama restored from FP side. | Completed | Non-maintainer | 3rd Party | Another Sub Contractor | Network Back Online | Hichem
168 | Sirti-WAN-R3-Ticket-148 | NA | 2026-04-12 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. | P011-Enc55-CE-01 |  |  | 25.2209722° 51.5862222° | Inside Doha | Critical | 2026-04-12 11:53 | 2026-04-12 11:56 | 3.0833 | 2026-04-12 11:56 | 2026-04-12 11:58 | 2.0333 | 5.1167 | As per the logs indicating a power interruption.Devices auto Restored before FLM reached the site. | Completed | Maintainer | N/a | N/a | Network Back Online | -
169 | Sirti-WAN-R3-Ticket-149 | NA | 2026-04-12 | Aaqib | Power Modules stopped working | Pwr3 & Pwr4 Modules Stopped Working | Routine PPM by P012 Tunnel team | P012-Enc97-UPE-02 |  |  | 25.1926322° 51.4542203° | Inside Doha | Critical | 2026-04-12 11:53 | 2026-04-12 11:58 | 5.3833 | 2026-04-12 11:58 | 2026-04-12 12:15 | 17.25 | 22.6333 | As per tunnel team, 1 Source is down due ongoing PPM activity. Modules are powered up and under observation. | Completed | Maintainer | N/a | N/a | Network Back Online | -
170 | Sirti-WAN-R3-Ticket-150 | NA | 2026-04-12 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. | P006-Enc17-UPE-02 P006-Enc17-CE-01 |  |  | 25.19542° 51.454° | Inside Doha | Critical | 2026-04-12 12:28 | 2026-04-12 12:30 | 1.8833 | 2026-04-12 12:30 | 2026-04-12 12:35 | 4.8333 | 6.7167 | Device rebooted during UPS testing activity. | Completed | Maintainer | N/a | N/a | Network Back Online | -
171 | Sirti-WAN-R3-Ticket-151 | NA | 2026-04-13 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | CB tripped at FP end | P012-ENC16-CE-01 | - | Zone 56 | 25.2250231° 51.5095445° | Inside Doha | Medium | 2026-04-13 09:55 | 2026-04-13 10:04 | 9 | 2026-04-13 11:14 | 2026-04-13 11:38 | 23.65 | 103 | no power in the cabinet. Tripped off main ITS-FP- breaker | Completed | Maintainer | N/a | N/a | Network Back Online | Najeeb
172 | Sirti-WAN-R3-Ticket-152 | NA | 2026-04-13 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-13 08:26 | 2026-04-13 08:30 | 4.1667 | 2026-04-13 08:30 | 2026-04-13 08:32 | 2.3 | 6.4667 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
173 | Sirti-WAN-R3-Ticket-153 | NA | 2026-04-13 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The UPS has input power, but there is no output power in FP | P005-ENC401-CE-01 |  | Zone 52 | 25.31049° 51.45271° | outside Doha | Critical | 2026-04-13 11:28 | 2026-04-13 11:30 | 2.1833 | 2026-04-13 12:50 | 2026-04-13 14:00 | 69.6833 | 151.95 | Power is available on the Kharama side and is connected to the UPS. The UPS has input power, but there is no output power. We will connect the Kahramaa power directly to the cabinet. | Completed | Non-Maintainer | N/a | N/a | Network Back Online | Irshad
174 | Sirti-WAN-R3-Ticket-154 | NA | 2026-04-13 | Sanket | Optical module Temperature too High | High Temperature | alarm is auto clear before visiting the site | DUK-ENC12-CE-01 | - |  | 25.4322949° 51.1106559° | outside Doha | Low | 2026-04-13 12:35 | 2026-04-13 12:44 | 9 | 2026-04-13 12:44 | 2026-04-13 13:40 | 55.6833 | 64.6833 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Network Back Online | -
175 | Sirti-WAN-R3-Ticket-155 | NA | 2026-04-14 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-14 09:40 | 2026-04-14 09:43 | 3 | 2026-04-14 09:43 | 2026-04-14 09:56 | 13.6667 | 16.6667 | As per Device Logs, there was power interruption at site.Auto restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Network Back Online | -
176 | Sirti-WAN-R3-Ticket-156 | NA | 2026-04-14 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The UPS has input power, but there is no output from the UPS, | P005-ENC401-CE-01 | - | Zone 52 | 25.31049° 51.45271° | outside Doha | Critical | 2026-04-14 10:21 | 2026-04-14 10:23 | 1.35 | 2026-04-14 10:26 | 2026-04-14 10:43 | 17.4167 | 21.7667 | Power is available from the Kahramaa side, and the UPS has incoming supply.There is no output from the UPS, and the display is not functioning. The cabinet was temporarily connected directly to Kahramaa power by Irshad’s team yesterday. After checking incoming power to the UPS is confirmed, but there is still no display and no output. The issue is suspected to be with the UPS itself, not the batteries | Completed | Non-maintainer | 3rd Party | RMC | Network Back Online | Najeeb
177 | Sirti-WAN-R3-Ticket-157 | NA | 2026-04-14 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | UPS CB Tripped | P040-CPE02-ENC21-DSW | - | Zone 57 | 25.189354 51.448508 | Inside Doha | Critical | 2026-04-14 09:42 | 2026-04-14 09:45 | 3.1833 | 2026-04-14 10:25 | 2026-04-14 11:18 | 53.1667 | 96.35 | UPS input circuit breaker tripped. The schema maintained by ITSQ | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Network Back Online | Patrick
178 | Sirti-WAN-R3-Ticket-158 | NA | 2026-04-14 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | UPS CB Tripped | P040-CPE02-ENC21-DSW | - | Zone 57 | 25.189354 51.448508 | Inside Doha | Critical | 2026-04-14 11:22 | 2026-04-14 11:24 | 2 | 2026-04-14 11:27 | 2026-04-14 11:34 | 7.4833 | 12.4833 | The ITSQ team bypass the UPS and directely connect the Kharamaa | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Network Back Online | Patrick
180 | Sirti-WAN-R3-Ticket-159 | NA | 2026-04-16 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption (alarm is auto clear before visiting the site) | P012-ENC17-CE-01 | - |  | 25.2323137° 51.5085231° | Inside Doha | Critical | 2026-04-16 07:32 | 2026-04-16 07:36 | 4 | 2026-04-16 07:36 | 2026-04-16 07:37 | 0.78333 | 4.7833 | As per the LOGS, device is rebooted (Power Interruption) | Completed | Maintainer | N/a | N/a | Devices Back Online | -
181 | Sirti-WAN-R3-Ticket-160 | NA | 2026-04-16 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption (alarm is auto clear before visiting the site) | P012-ENC33-CE-01 | - |  | 25.2282194° 51.5019836° | Inside Doha | Critical | 2026-04-16 08:37 | 2026-04-16 08:40 | 3 | 2026-04-16 08:40 | 2026-04-16 08:44 | 3.6 | 6.6 | As per the LOGS, device is rebooted (Power Interruption) | Completed | Maintainer | N/a | N/a | Devices Back Online | -
182 | Sirti-WAN-R3-Ticket-161 | NA | 2026-04-16 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption (alarm is auto clear before visiting the site) | P002-ENC01-CE-01 | - |  | 25.2632875° 51.4952573° | Inside Doha | Critical | 2026-04-16 14:17 | 2026-04-16 14:23 | 5.75 | 2026-04-16 14:23 | 2026-04-16 14:26 | 3 | 8.75 | As per the LOGS, device is rebooted (Power Interruption) | Completed | Maintainer | N/a | N/a | Devices Back Online | -
183 | Sirti-WAN-R3-Ticket-162 | NA | 2026-04-16 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | There was a switch-off at the rectifier site on UPS 3 and UPS 4. After switching them back on, the node was powered up | P002-ENC01-CE-01 |  |  | 25.2632875° 51.4952573° | Inside Doha | Critical | 2026-04-16 14:59 | 2026-04-16 15:01 | 2.05 | 2026-04-16 15:01 | 2026-04-16 15:07 | 6.2 | 8.25 | All four UPS units and battery sets were checked for input and output voltage, and UPS units are reset and monitored for a few hours; the node operated continuously without failure | Completed | Non-maintainer | 3rd Party | RMC | Devices Back Online | -
184 | Sirti-WAN-R3-Ticket-163 | NA | 2026-04-16 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | - No power on cabinet - UPS3 and UPS4 CBs were tripped - UPS1 and UPS2 are in fault mode | P002-ENC01-CE-01 |  |  | 25.2632875° 51.4952573° | Inside Doha | Critical | 2026-04-16 15:18 | 2026-04-16 15:22 | 4.25 | 2026-04-16 15:55 | 2026-04-16 16:13 | 18.1833 | 55.4333 | - FLM found no power on the cabinet as the UPS CB tripped. - Device restored after switching ON the UPS CB. - Restarted the UPS1 and UPS2 and cleared the fault | Completed | Non-maintainer | 3rd Party | RMC | Devices Back Online | Sanjeewa
185 | Sirti-WAN-R3-Ticket-164 | NA | 2026-04-17 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Main CB Tripped | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-17 14:22 | 2026-04-17 14:25 | 3.1667 | 2026-04-17 14:53 | 2026-04-17 14:59 | 5.7333 | 36.8167 | The circuit breaker in the cabinet has tripped. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Eric
186 | Sirti-WAN-R3-Ticket-165 | NA | 2026-04-18 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC compressor is faulty and needs replacement. Additionally, the system requires a gas refill and a complete servicing | P023C1-ENC01-UPE-01 | - |  | 25.111748° 51.583897° | Outside Doha | Critical | 2026-04-18 09:53 | 2026-04-18 09:59 | 5.7333 | 2026-04-18 10:40 | 2026-04-18 10:50 | 9.7667 | 57.0167 | FLM isited the site and checked dual A/C system in WAN cabinet. AC1: Gas leakage found at pin valve → replaced valve, refilled gas, cleaned unit → tested OK (cooling normal). AC2: Compressor found faulty → replaced compressor (SECOP SC15G), refilled gas, cleaned unit → tested OK (cooling normal). Both A/C units are now operational and cooling properly. | Completed | Maintainer | N/a | N/a | Alarm Cleared | Eric
187 | Sirti-WAN-R3-Ticket-166 | NA | 2026-04-18 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC compressor is faulty and needs replacement. Additionally, the system requires a gas refill and a complete servicing | P060-ENC179-UPE-02 |  |  | 25.639484° 51.491537° | Outside Doha | Critical | 2026-04-18 14:41 | 2026-04-18 14:44 | 3.65 | 2026-04-18 15:20 | 2026-04-18 15:29 | 8.1833 | 47.8333 | FLM visited the site and checked dual A/C system in WAN cabinet. AC1: Gas leakage found at pin valve → replaced valve, refilled R134a gas, cleaned unit → tested OK (cooling normal). AC2: Compressor missing → installed new compressor (SECOP SC15G), refilled R134a gas, cleaned unit → tested OK (cooling normal). Both A/C units are now operational and cooling properly. | Completed | Maintainer | N/a | N/a | Alarm Cleared | Eric
188 | Sirti-WAN-R3-Ticket-167 | NA | 2026-04-18 | Sanket | Power Modules stopped working | Power module powered off | KAHRAMAA power interruption. | P004- TMC-NPE and P004_DWDM | - | Zone 53 | 25.319385 51.352255 | Outside Doha | Critical | 2026-04-18 19:21 | 2026-04-18 19:26 | 5.5833 | 2026-04-18 20:13 | 2026-04-18 20:33 | 19.4167 | 71.7333 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Sanjeewa
189 | Sirti-WAN-R3-Ticket-168 | NA | 2026-04-18 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | RCCB CB Tripped | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-18 23:43 | 2026-04-18 23:45 | 1.6167 | 2026-04-19 00:35 | 2026-04-19 00:53 | 18.3833 | 70 | The circuit breaker in the cabinet has tripped due to unstable power. FLM switched on the RCCB. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Ghulam
190 | Sirti-WAN-R3-Ticket-169 | NA | 2026-04-19 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | GE1/0/9 toward Local Node was down | DUK-ENC06-CE-01 | - |  | 25.3954062° 51.1985851° | Outside Doha | Critical | 2026-04-19 00:31 | 2026-04-19 00:38 | 7.4667 | 2026-04-19 00:31 | 2026-04-19 01:08 | 37.3 | 37.3 | Alarm is auto clear before visiting the site | Completed | Maintainer | N/a | N/a | Port is up and alarm cleared
191 | Sirti-WAN-R3-Ticket-170 | NA | 2026-04-19 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity by FLM to check and verify the power cable from service cabinet to IE5000-1003 enclosure | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-19 01:47 | 2026-04-19 01:49 | 2.1167 | 2026-04-19 01:47 | 2026-04-19 01:54 | 7.3333 | 7.3333 | Checked and reconnected the power cable inside the IE5000-1003 service cabinet | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Ghulam
192 | Sirti-WAN-R3-Ticket-171 | NA | 2026-04-19 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity by FLM to check and verify the power cable inside IE5000-1003 enclosure | IE5000-1003 | - | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-19 02:54 | 2026-04-19 03:03 | 8.6167 | 2026-04-19 02:54 | 2026-04-19 03:19 | 24.2167 | 24.2167 | Checked and reconnected the power cable inside the IE5000-1003 Enclosure | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Ghulam
193 | Sirti-WAN-R3-Ticket-172 | NA | 2026-04-19 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. | IE5000-1003 |  | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-19 08:57 | 2026-04-19 08:59 | 1.4833 | 2026-04-19 08:57 | 2026-04-19 09:00 | 3.3 | 3.3 | As per the LOGS, device is rebooted (Power Interruption) | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
194 | Sirti-WAN-R3-Ticket-173 | NA | 2026-04-19 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Power interruption due to CB Tripping | IE5000-1003 |  | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-19 09:10 | 2026-04-19 09:11 | 0.78333 | 2026-04-19 09:10 | 2026-04-19 09:15 | 4.3833 | 4.3833 | Reconnect the AC directly to the incoming power supply (instead of through the ELCB) to prevent the node from going down due to AC short faults | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
195 | Sirti-WAN-R3-Ticket-174 | NA | 2026-04-19 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC compressor is faulty and needs replacement. Additionally, the system requires a gas refill and a complete servicing | P010-Enc01-CE-01 |  |  | 25.1398815° 51.4073931 | Outside Doha | Critical | 2026-04-19 09:20 | 2026-04-19 09:23 | 2.9167 | 2026-04-19 10:51 | 2026-04-19 10:54 | 2.7833 | 93.6 | Faulty compressor was replaced with a new LG GJS222PMA model (220–250V, 50Hz, 1PH LRA42.5), along with a new 35 MFD capacitor and copper dry filter. The condenser and compressor were cleaned using nitrogen gas, R22 refrigerant was filled, and the thermostat temperature was set. All AC parts were thoroughly cleaned with a blower and towels, and after testing, the unit was observed to be cooling effectively and operating in good condition | Completed | Maintainer | N/a | N/a | Alarm Cleared | Rizwan
196 | Sirti-WAN-R3-Ticket-175 | NA | 2026-04-19 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | main CB is tripped at cabinet side | P028C2-ENC-07-CE-01.omc.local |  | Zone 27 | 25.2827572° 51.5448455° | Inside Doha | Critical | 2026-04-19 19:24 | 2026-04-19 19:25 | 1.25 | 2026-04-19 20:08 | 2026-04-19 20:18 | 10.45 | 54.7 | FLM switched on tripped main CB at cabinet side | Completed | Maintainer | N/a | N/a | Alarm Cleared | Hassan
197 | Sirti-WAN-R3-Ticket-176 | NA | 2026-04-19 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | device down flapped for 2 min and auto-restored | DUK-ENC30-CE-01 |  |  | 25.4637854° 50.930279° | Outside Doha | Critical | 2026-04-19 19:35 | 2026-04-19 19:37 | 2.25 | 2026-04-19 19:37 | 2026-04-19 19:37 | 0.25 | 2.5 | device auto restored after 2 min | Completed | Maintainer | N/a | N/a | Alarm Cleared | -
198 | Sirti-WAN-R3-Ticket-177 | NA | 2026-04-19 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | devices wend down while team is working for fixing faulty AC | P010-ENC01-CE-01 P010-ENC01-UPE01 |  |  | 25.1398815° 51.4073931° | Outside Doha | Critical | 2026-04-19 21:40 | 2026-04-19 21:42 | 2.1833 | 2026-04-19 21:43 | 2026-04-19 21:47 | 3.5833 | 6.7667 | devices wend down while team is working for fixing faulty AC | Completed | Maintainer | N/a | N/a | Alarm Cleared | Eric
199 | Sirti-WAN-R3-Ticket-178 | NA | 2026-04-19 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | device down flapped for 10 min and auto-restored | IE5000-1003.ashghal |  |  | 25.30450151 51.51807558 | Inside Doha | Critical | 2026-04-19 23:39 | 2026-04-19 23:42 | 2.7167 | 2026-04-19 23:42 | 2026-04-19 23:49 | 7.1 | 9.8167 | device down flapped for 10 min and auto-restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
200 | Sirti-WAN-R3-Ticket-179 | NA | 2026-04-20 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC functioning system is not working properly | P010-ENC01-CE-01 |  |  | 25.1398815° 51.4073931 | Outside Doha | Critical | 2026-04-20 10:47 | 2026-04-20 10:51 | 3.75 | 2026-04-20 10:59 | 2026-04-20 11:49 | 50.05 | 61.8 | FLM checked and found the AC condenser and evaporator were blocked. FLM cleaned and flushed them using 141B liquid, then dried them with nitrogen gas and a vacuum pump. After reinstalling, we refilled with R22 gas and set the temperature. Finally, we cleaned all AC parts with a blower | Completed | Non-maintainer | Defect | Fixing of Defect | Alarm Cleared | Khadar
201 | Sirti-WAN-R3-Ticket-180 | NA | 2026-04-20 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Polaris team is working on site changing power cable | SAL-ENC09-CE-01 |  |  | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-04-20 15:13 | 2026-04-20 15:16 | 3.2833 | 2026-04-20 15:21 | 2026-04-20 15:38 | 17.2333 | 25.5167 | FLM reach the site and found Polaris team is working on site for changing power cable | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Devices Back Online | masthan
202 | Sirti-WAN-R3-Ticket-181 | NA | 2026-04-20 | Abubaker | Link Down (GE1/0/9 toward the local device) | LAN Link Down | Port Auto restored before FLM reach the site | DUK-ENC12-CE-01 |  |  | 25.4302156° 51.1497491° | Outside Doha | Critical | 2026-04-20 23:10 | 2026-04-20 23:17 | 6.6167 | 2026-04-20 23:17 | 2026-04-20 23:34 | 16.55 | 23.1667 | Port GE1/0/9 flapped during the incident and Auto restored before FLM reach to the site | Completed | Maintainer | N/a | N/a | Alarm Cleared | -
203 | Sirti-WAN-R3-Ticket-182 | NA | 2026-04-21 | Abubaker | Link Down (GE1/0/9 toward the local device) | LAN Link Down | Port Auto restored before FLM reach the site | DUK-ENC16-CE-01 |  |  | 25.4322949° 51.1106559° | Outside Doha | Critical | 2026-04-21 00:46 | 2026-04-21 00:55 | 9.3333 | 2026-04-21 00:55 | 2026-04-21 01:20 | 24.9667 | 34.3 | Port GE1/0/9 flapped during the incident and Auto restored before FLM reach to the site | Completed | Maintainer | N/a | N/a | Alarm Cleared | -
204 | Sirti-WAN-R3-Ticket-183 | NA | 2026-04-21 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P012-ENC12-CE-01 | - |  | 25.2212138° 51.5169228° | Inside Doha | Critical | 2026-04-21 09:55 | 2026-04-21 09:56 | 1 | 2026-04-21 09:56 | 2026-04-21 09:59 | 3.1333 | 4.1333 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
205 | Sirti-WAN-R3-Ticket-184 | NA | 2026-04-21 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P012-ENC12-CE-01 | - | Zone 56 | 25.2212138° 51.5169228° | Inside Doha | Critical | 2026-04-21 10:57 | 2026-04-21 10:59 | 2 | 2026-04-21 11:45 | 2026-04-21 11:47 | 1.75 | 49.75 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
206 | Sirti-WAN-R3-Ticket-185 | NA | 2026-04-22 | Sanket | Link Down | LAN Link Down | GE 1/13 down towards 16041-P12-BSW | P012-ENC12-CE-01 | - | Zone 56 | 25.2212138° 51.5169228° | Inside Doha | Critical | 2026-04-22 06:20 | 2026-04-22 06:34 | 14 | 2026-04-22 07:10 | 2026-04-22 07:41 | 30.95 | 80.95 | The Link is down towards LAN | Completed | Maintainer | N/a | N/a | Alarm Cleared | Najeeb
207 | Sirti-WAN-R3-Ticket-185 | NA | 2026-04-22 | Sanket | Link Down | WAN Link Down | Port TE 1/28 towards P012-ENC09-UPE-01 port 40GE 4/0/1 is down | P012-ENC12-CE-01 | - | Zone 56 | 25.2212138° 51.5169228° | Inside Doha | Critical | 2026-04-22 06:20 | 2026-04-22 06:34 | 14 | 2026-04-22 07:10 | 2026-04-22 07:41 | 30.95 | 80.95 | Fiber Patch chord raplaced | Completed | Maintainer | N/a | N/a | Alarm Cleared | Najeeb
208 | Sirti-WAN-R3-Ticket-186 | NA | 2026-04-22 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P040-CPE01-ENC01-DSW | - |  | 25.179715 51.408779 | Inside Doha | Critical | 2026-04-22 13:16 | 2026-04-22 13:18 | 1.45 | 2026-04-22 13:18 | 2026-04-22 13:20 | 2.0333 | 3.4833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Devices Back Online | -
209 | Sirti-WAN-R3-Ticket-187 | NA | 2026-04-22 | Aaqib | Link Down | LAN Link Down | Port GE 1/0/9 connected towards Enc34-Local-Node went down | Duk-Enc34-CE-01 |  |  | 25.4537767° 50.8835078° | Outside Doha | Critical | 2026-04-22 22:18 | 2026-04-22 22:20 | 2 | 2026-04-22 22:45 | 2026-04-22 22:49 | 4 | 31 | FLM checked ethernet and POE connections for the camera and found all connections are normally fixed ,suspected weather condition | Completed | Non-maintainer | Environmental | High wind Event | Alarm Cleared | farouk
210 | Sirti-WAN-R3-Ticket-188 | NA | 2026-04-23 | Adel | Power Modules stopped working | Power module powered off | no abnormal observations on site | SAL-ENC32-CE-01 | - | - | 25.1165799° 51.1812367° | Outside Doha | Critical | 2026-04-23 21:48 | 2026-04-23 21:54 | 6 | 2026-04-23 21:54 | 2026-04-23 22:44 | 50 | 56 | Alarm is auto clear before reaching the site , FLM visited and checked all power connections and found all connections are normally connected | Completed | Maintainer | N/a | N/a | Alarm Cleared | umair
211 | Sirti-WAN-R3-Ticket-189 | NA | 2026-04-25 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption. | IE5000-1003 |  | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-25 08:24 | 2026-04-25 08:25 | 1 | 2026-04-25 08:25 | 2026-04-25 08:27 | 1.9833 | 2.9833 | Kahramaa planned shutdown | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
212 | Sirti-WAN-R3-Ticket-190 | NA | 2026-04-25 | Sanket | Link Down | LAN Link Down | Team found no power in cabinet | SAL-ENC63-CE-01 | - |  | 25.3344995° 51.5180512 | Outside Doha | Critical | 2026-04-25 13:09 | 2026-04-25 13:12 | 3 | 2026-04-25 13:58 | 2026-04-25 16:15 | 137.4667 | 186.3167 | LAN cabinet main breaker tripped due to street light CB fault; devices restored after Cabinet breaker reset | Completed | Maintainer | N/a | N/a | Alarm Cleared | Khadar
213 | Sirti-WAN-R3-Ticket-191 | NA | 2026-04-25 | Sanket | Link Down | WAN Link Down | FLM found fiber cable was burnt inside the ITS chamber, with the fault located about 390 meters from JN-6401. The suspected cause is a fire originating from an advertisement board installed above the chamber, which resulted in damage to the PWA fiber cable. | P003-ENC40-UPE-02 |  |  | 25.3344995° 51.5180512° | Inside Doha | Critical | 2026-04-25 13:07 | 2026-04-25 13:13 | 5.75 | 2026-04-25 14:33 | 2026-04-28 00:02 | 3449.1667 | 3534.5833 | installed new fiber cable & Spliced 24 core in enclosure chamber 11 and JN-6401 | Completed | Non-maintainer | 3rd Party | Fire | Alarm Cleared | Najeeb
214 | Sirti-WAN-R3-Ticket-192 | NA | 2026-04-25 | Aaqib | Link Down | LAN Link Down | 1x10G Link (TE 1/0/10) went down and auto restored | P005-TCR-CE-02 |  |  | 25.3199307 51.447548 | Outside Doha | Critical | 2026-04-25 17:04 | 2026-04-25 17:07 | 3 | 2026-04-25 17:07 | 2026-04-25 17:10 | 2.8 | 5.8 | Link auto restored after 5min. | Completed | Non-maintainer | 3rd Party | GBDG Contractor | Alarm Cleared | -
215 | Sirti-WAN-R3-Ticket-193 | NA | 2026-04-25 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P059C1-N3-Enc20-CE-01 |  |  | 25.44194931° 51.41112813° | Outside Doha | Critical | 2026-04-25 18:41 | 2026-04-25 18:44 | 2.55 | 2026-04-25 18:44 | 2026-04-25 18:47 | 3.4 | 5.95 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
216 | Sirti-WAN-R3-Ticket-194 | NA | 2026-04-26 | Aaqib | Link Down | LAN Link Down | Team found no power in cabinet | DUK-ENC12-CE-01 |  |  | 25.4302156° 51.1497491° | Outside Doha | Critical | 2026-04-26 08:01 | 2026-04-26 08:04 | 2.8667 | 2026-04-26 08:50 | 2026-04-26 10:12 | 81.4167 | 130.0833 | Planned activity by kahrama for transformer replacement at FP | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Rizwan
217 | Sirti-WAN-R3-Ticket-195 | NA | 2026-04-26 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P023C3-ENC174-UPE-02 P023C3-ENC174-CE-02 |  |  | 25.0168866° 51.490473° | Outside Doha | Critical | 2026-04-26 12:33 | 2026-04-26 12:35 | 2.35 | 2026-04-26 12:35 | 2026-04-26 12:38 | 2.6833 | 5.0333 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
218 | Sirti-WAN-R3-Ticket-196 | NA | 2026-04-26 | Aaqib | Link Down | LAN Link Down | KAHRAMAA power interruption | SAL-ENC63-CE-01 |  |  | 24.8301249° 50.8705931° | Outside Doha | Critical | 2026-04-26 12:37 | 2026-04-26 12:42 | 4.5333 | 2026-04-26 12:42 | 2026-04-26 12:49 | 7.4167 | 11.95 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
219 | Sirti-WAN-R3-Ticket-197 | NA | 2026-04-26 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | PLanned activity for UPS battery replacment | P010-ENC61-CE-01 |  |  | 25.1700975° 51.4699752° | Outside Doha | Critical | 2026-04-26 23:26 | 2026-04-26 23:27 | 0.9 | 2026-04-26 23:27 | 2026-04-27 00:30 | 63.0167 | 63.9167 | UPS batteries replacement activity was successfully completed | Completed | Non-maintainer | Planned Activity | UPS defect also | Alarm Cleared | Farooq
220 | Sirti-WAN-R3-Ticket-198 | NA | 2026-04-27 | Adel | Link Down | LAN Link Down | corevit company team is performing activity at SOC P007 | P007C2-170018-R2-CSW |  |  | 25.2942202 51.4657002 | Inside Doha | Critical | 2026-04-27 00:19 | 2026-04-27 00:23 | 3.8333 | 2026-04-27 01:18 | 2026-04-27 02:17 | 59 | 117.8333 | multiple ports are flapped due to corevit company activity at control room | Completed | Non-maintainer | 3rd Party | corevit contractor | Alarm Cleared | umair
221 | Sirti-WAN-R3-Ticket-199 | NA | 2026-04-27 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | SAL-ENC63-CE-01 |  |  | 24.8301249° 50.8705931° | Outside Doha | Critical | 2026-04-27 07:09 | 2026-04-27 07:12 | 2.6 | 2026-04-27 07:12 | 2026-04-27 07:14 | 2.5167 | 5.1167 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
222 | Sirti-WAN-R3-Ticket-200 | NA | 2026-04-27 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC CB was tripped | P059C1-ENC23-UPE-02 |  |  | 25.4516333° 51.4090805° | Outside Doha | Critical | 2026-04-27 12:41 | 2026-04-27 12:50 | 9.2167 | 2026-04-27 13:52 | 2026-04-27 14:01 | 8.1667 | 79.5167 | The FLM team serviced one A/C and confirmed it is working properly. The other A/C remains off, and its compressor replacement is scheduled. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan / Eric
223 | Sirti-WAN-R3-Ticket-201 | NA | 2026-04-27 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | CB at FP side tripped | P059C1-ENC23-UPE-02 P059C1-ENC23-CE-01 |  |  | 25.4516333° 51.4090805° | Outside Doha | Critical | 2026-04-27 14:07 | 2026-04-27 14:11 | 3.3167 | 2026-04-27 14:09 | 2026-04-27 14:22 | 13 | 14.5167 | Main CB at FP was tripped. Devices restored after turning CB ON | Completed | Maintainer | N/a | N/a | Devices Back Online | Rizwan
224 | Sirti-WAN-R3-Ticket-202 | NA | 2026-04-27 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC CB was tripped | P059C1-ENC04-UPE-01 |  |  | 25.3653937° 51.4467471° | Outside Doha | Critical | 2026-04-27 14:19 | 2026-04-27 14:25 | 5.7167 | 2026-04-27 14:45 | 2026-04-27 14:55 | 9.4167 | 35.3167 | The FLM team performed general servicing for the A/C and ensured that the A/C system is working properly | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan / Eric
225 | Sirti-WAN-R3-Ticket-203 | NA | 2026-04-28 | Aaqib | Link Down | WAN Link Down | Optical Rx power for the uplink was very low at P003-ENC41 | IE5000-6009 |  |  | 25.3233945337° 51.5360444444° | Inside Doha | Critical | 2026-04-28 08:22 | 2026-04-28 08:25 | 2.55 | 2026-04-28 09:02 | 2026-04-28 22:18 | 796 | 836 | The FLM team inspected the uplink fiber route, cleaned it, and adjusted the bends at P003-ENC41, which improved the optical power levels and brought the port up. An OTDR test activity has been scheduled to further optimize the optical power. | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Irshad
226 | Sirti-WAN-R3-Ticket-204 | NA | 2026-04-28 | Aaqib | CPU Temperature too high | High Temperature | Current temperature is 56°C at SFU board 6 | P008C3-ENC25-UPE-02 |  |  | 25.2341068° 51.50261° | Inside Doha | Critical | 2026-04-28 13:37 | 2026-04-28 13:42 | 5.0333 | 2026-04-28 15:00 | 2026-04-28 15:23 | 22.9667 | 106 | There is issue with AC and schema maintained by Salam Tech | Completed | Non-maintainer | 3rd Party | Salam Tech | Alarm Cleared | -
227 | Sirti-WAN-R3-Ticket-205 | NA | 2026-04-28 | Sanket | Power Modules stopped working | Power module powered off | Power interruption (CB tripped) in control room | P003_DWDM |  |  | 25.3730597 51.5247872 | Inside Doha | Critical | 2026-04-28 15:13 | 2026-04-28 15:26 | 13 | 2026-04-28 15:26 | 2026-04-28 15:40 | 13.4333 | 26.4333 | As per discussion with Mr.Tahir (EGIS-Control room), The CB is tripped near the fire alarm. No service impact as device working on redundant power modules | Completed | Non-maintainer | 3rd Party | Egis | Alarm Cleared | -
228 | Sirti-WAN-R3-Ticket-206 | NA | 2026-04-28 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | MCB tripped at ITS FP | P029C2-ENC05-CE-01 |  | Zone 38 | 25.281278° 51.503972° | Inside Doha | Critical | 2026-04-28 16:57 | 2026-04-28 17:03 | 5.9167 | 2026-04-28 17:39 | 2026-04-28 18:03 | 23.85 | 65.7667 | The MCB had tripped at the ITS FP. The field engineer turned it back ON, and the device is now reachable. | Completed | Maintainer | N/a | N/a | Devices Back Online | Masthanbasha
229 | Sirti-WAN-R3-Ticket-207 | NA | 2026-04-29 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | IE5000-1003 |  | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-04-29 11:20 | 2026-04-29 11:25 | 4.7333 | 2026-04-29 11:25 | 2026-04-29 11:36 | 11.6167 | 16.35 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
230 | Sirti-WAN-R3-Ticket-208 | NA | 2026-04-30 | Abubaker | Link Down | LAN Link Down | Port Auto restored before FLM reach the site | SAL-ENC67-CE-01 |  |  | 24.7761642° 50.8665552° | Outside Doha | Critical | 2026-04-30 04:07 | 2026-04-30 04:18 | 11.2667 | 2026-04-30 04:18 | 2026-04-30 04:31 | 13.4333 | 24.7 | Port GE1/0/9 Auto restored before FLM reach to the site | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | -
231 | Sirti-WAN-R3-Ticket-209 | NA | 2026-05-01 | Abubaker | Link Down | LAN Link Down | Port Auto restored before FLM reach the site | SAL-ENC20-CE-01 |  |  | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-01 04:34 | 2026-05-01 04:44 | 9.55 | 2026-05-01 04:44 | 2026-05-01 05:00 | 15.5667 | 25.1167 | Port GE1/0/9 Auto restored before FLM reach to the site | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | -
232 | Sirti-WAN-R3-Ticket-210 | NA | 2026-05-01 | Aaqib | Link Down | LAN Link Down | KAHRAMAA power interruption | SAL-ENC26-CE-01 |  |  | 25.1435454° 51.2478413° | Outside Doha | Critical | 2026-05-01 07:36 | 2026-05-01 07:42 | 5.7667 | 2026-05-01 07:42 | 2026-05-01 07:45 | 3.0333 | 8.8 | SAL-ENC26-CE-01 Port 25GE 1/0/4 connected to (S-Node-25) was down due to Kahramaa planned shutdown | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
233 | Sirti-WAN-R3-Ticket-211 | NA | 2026-05-01 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P011-Enc01-CE-01 |  |  | 25.1812793° 51.5013254° | Inside Doha | Critical | 2026-05-01 14:25 | 2026-05-01 14:28 | 3.5667 | 2026-05-01 14:28 | 2026-05-01 14:34 | 5.4833 | 9.05 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
234 | Sirti-WAN-R3-Ticket-212 | NA | 2026-05-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | There was no power inside the cabinet due to high temperature at cabinet | P006-ECN17-UPE-02 P006-ENC17-CE-01 |  |  | 25.19542° 51.454° | Inside Doha | Critical | 2026-05-01 16:14 | 2026-05-01 16:17 | 3.3667 | 2026-05-01 16:47 | 2026-05-01 17:03 | 16.3333 | 49.7 | FLM team kept the cabinet open to cool down and scheduled for A/C system inspection | Completed | Non-maintainer | Defect | AC | Devices Back Online | Salem Haj
235 | Sirti-WAN-R3-Ticket-213 | NA | 2026-05-02 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | IE5000-1003 |  | Zone 60 | 25.30462 51.51743 | Inside Doha | Critical | 2026-05-02 10:18 | 2026-05-02 10:22 | 4.4 | 2026-05-02 10:22 | 2026-05-02 10:24 | 1.6167 | 6.0167 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
236 | Sirti-WAN-R3-Ticket-214 | NA | 2026-05-02 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | There was no output power from the UPS due to high temperature inside the cabinet | P006-ECN17-UPE-02 P006-ENC17-CE-01 |  |  | 25.19542° 51.454° | Inside Doha | Critical | 2026-05-02 15:13 | 2026-05-02 15:16 | 2.8333 | 2026-05-02 15:45 | 2026-05-02 15:58 | 13.2833 | 45.1167 | FLM team restarted the UPS | Completed | Non-maintainer | Defect | AC | Devices Back Online | Hassan
237 | Sirti-WAN-R3-Ticket-215 | NA | 2026-05-02 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | A/C system was not working properly, FLM team was on site to repair the A/C system | P006-ECN17-UPE-02 P006-ENC17-CE-01 |  |  | 25.19542° 51.454° | Inside Doha | Critical | 2026-05-02 19:57 | 2026-05-02 19:59 | 2.3167 | 2026-05-02 20:09 | 2026-05-02 21:27 | 77.6333 | 89.95 | Team replaced faulty Airconditioner condenser fan | Completed | Non-maintainer | Defect | AC | Devices Back Online | Eric
238 | Sirti-WAN-R3-Ticket-216 | NA | 2026-05-03 | Aaqib | CPU Temperature too high | High Temperature | Threshold temperature was set high | P023C1-ENC01-UPE-01 |  |  | 25.111748° 51.583897° | Outside Doha | Critical | 2026-05-03 09:04 | 2026-05-03 09:09 | 5 | 2026-05-03 09:47 | 2026-05-03 09:50 | 2.7833 | 45.9167 | The required temperature in the Cabinet has been set as per the standard level | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Ghulam
239 | Sirti-WAN-R3-Ticket-217 | NA | 2026-05-03 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | MCB was tripped inside WAN Cabinet | P028C2-ENC-01-CE-01 |  |  | 25.2839108° 51.5496128° | Inside Doha | Critical | 2026-05-03 09:47 | 2026-05-03 09:55 | 7.1833 | 2026-05-03 10:18 | 2026-05-03 10:21 | 3.1167 | 33.5 | Device restored after turning on MCB inside cabinet | Completed | Maintainer | N/a | N/a | Devices Back Online | Irshad
240 | Sirti-WAN-R3-Ticket-218 | NA | 2026-05-03 | Aaqib | CPU Temperature too high | High Temperature | Gas leakage in the AC pipe and Compressor faulty | P060-ENC179-UPE-02 |  |  | 25.639484° 51.491537° | Outside Doha | Critical | 2026-05-03 10:20 | 2026-05-03 10:24 | 3.8 | 2026-05-03 11:28 | 2026-05-03 11:36 | 7.7667 | 75.65 | Detected and repaired refrigerant leakage in the capillary tube, replaced the filter drier, performed system vacuuming, refilled R134a refrigerant, and completed general servicing of the unit. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Ghulam
241 | Sirti-WAN-R3-Ticket-219 | NA | 2026-05-03 | Aaqib | CPU Temperature too high | High Temperature | AC Compressor faulty | P011-Enc26-CE-01 |  |  | 25.19975° 51.541528° | Inside Doha | Critical | 2026-05-03 10:53 | 2026-05-03 10:58 | 5.1833 | 2026-05-03 12:41 | 2026-05-03 12:57 | 15.35 | 123.4667 | The compressor, fan, and 40+5 capacitor were replaced | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
242 | Sirti-WAN-R3-Ticket-220 | NA | 2026-05-03 | Aaqib | CPU Temperature too high | High Temperature | Threshold temperature was set high | P023C3-ENC174-UPE-02 |  |  | 25.0168866° 51.490473° | Outside Doha | Critical | 2026-05-03 12:17 | 2026-05-03 12:22 | 5.1333 | 2026-05-03 14:15 | 2026-05-03 14:18 | 2.75 | 120.7333 | Cabinet temperature normalized after setting temperatures parameters in AC controller | Completed | Non-maintainer | Defect | AC | Devices Back Online | Ghulam
243 | Sirti-WAN-R3-Ticket-221 | NA | 2026-05-03 | Aaqib | CPU Temperature too high | High Temperature | Schema Under Salam technology | P008C3-Enc01-UPE-01 |  |  | 25.2614822° 51.4801647° | Inside Doha | Critical | 2026-05-03 13:45 | 2026-05-03 13:51 | 6.25 | 2026-05-03 14:07 | 2026-05-03 14:17 | 10.2 | 32.2833 | Schema Under Salam tech. Escalated to Mr.Salman | Completed | Non-maintainer | 3rd Part (Salam Tech) | N/a | Alarm Cleared | -
244 | Sirti-WAN-R3-Ticket-222 | NA | 2026-05-03 | Aaqib | CPU Temperature too high | High Temperature | Threshold temperature was set high | P010-Enc01-CE-01 |  |  | 25.1398815° 51.4073931° | Outside Doha | Critical | 2026-05-03 14:16 | 2026-05-03 14:19 | 2.65 | 2026-05-03 14:35 | 2026-05-03 14:46 | 11.1667 | 29.95 | The required temperature in the Cabinet has been set as per the standard level | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Ghulam
245 | Sirti-WAN-R3-Ticket-223 | NA | 2026-05-03 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | SAL-ENC09-CE-01 |  |  | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-05-03 20:33 | 2026-05-03 20:35 | 1.65 | 2026-05-03 20:33 | 2026-05-03 20:35 | 1.9833 | 1.9833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
246 | Sirti-WAN-R3-Ticket-224 | NA | 2026-05-04 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | IE5000-1003 |  | Zone 60 | 25.30462° 51.51743° | Inside Doha | Critical | 2026-05-04 12:27 | 2026-05-04 12:32 | 5 | 2026-05-04 12:32 | 2026-05-04 12:50 | 17 | 22 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
247 | Sirti-WAN-R3-Ticket-225 | NA | 2026-05-04 | Aaqib | Optical module Temperature too High | High Temperature | No AC installed in cabinet and Exhaust Fan not working | IE5000-1702 |  |  | 25.2833249904° 51.551376977° | Inside Doha | Critical | 2026-05-04 13:27 | 2026-05-04 13:29 | 2.6 | 2026-05-04 13:57 | 2026-05-04 14:03 | 6.1667 | 36.15 | FLM replaced faulty exhaust FAN | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Irshad/
248 | Sirti-WAN-R3-Ticket-226 | NA | 2026-05-04 | Aaqib | Optical module Temperature too High | High Temperature | Threshold temperature was set high | 22FEB-ENC01-CE-01 |  |  | 25.2453756° 51.5148756° | Inside Doha | Critical | 2026-05-04 14:40 | 2026-05-04 14:42 | 1.75 | 2026-05-04 16:40 | 2026-05-04 16:47 | 6.4667 | 126.4667 | alarm is auto cleared before reaching the site , FLM visited and set the temperature thermostat of the AC from 32C to 28C | Completed | Non-maintainer | Defect | N/a | Alarm Cleared | Khadar
249 | Sirti-WAN-R3-Ticket-227 | NA | 2026-05-05 | Sanket | Power Modules stopped working | Power module powered off | KAHRAMAA power interruption | P003-ENC40-UPE-02 |  |  | 25.3344995° 51.5180512° | Inside Doha | Critical | 2026-05-05 04:50 | 2026-05-05 04:51 | 1 | 2026-05-05 04:51 | 2026-05-05 04:52 | 1.3 | 2.3 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
250 | Sirti-WAN-R3-Ticket-228 | NA | 2026-05-05 | Aaqib | Link down | LAN Link Down | Auto Restored | RAA-ENC01-CE-01 |  |  | 25.284123° 51.5558539° | Inside Doha | Critical | 2026-05-05 11:28 | 2026-05-05 11:35 | 7.3833 | 2026-05-05 11:35 | 2026-05-05 12:01 | 25.7333 | 33.1167 | Alarm Auto Restored | Completed | Non-maintainer | N/a | N/a | Alarm Cleared | Hichem
251 | Sirti-WAN-R3-Ticket-229 | NA | 2026-05-05 | Aaqib | CPU Temperature too high | High Temperature | AC working but not cooling | P023C3-ENC174-UPE-02 |  |  | 25.0168866° 51.490473° | Outside Doha | Critical | 2026-05-05 12:03 | 2026-05-05 12:13 | 9.95 | 2026-05-05 13:01 | 2026-05-05 13:21 | 20.4667 | 78.6167 | The compressor cable had been disconnected; we simply reconnected it | Completed | Non-maintainer | Defect | N/a | Alarm Cleared | Eric
252 | Sirti-WAN-R3-Ticket-230 | NA | 2026-05-05 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P007C1-ENC31-UPE-01 |  |  | 25.306727 51.411587 | Inside Doha | Critical | 2026-05-05 12:59 | 2026-05-05 13:09 | 10.55 | 2026-05-05 13:09 | 2026-05-05 13:36 | 27.0833 | 37.6333 | Kahramaa planned shutdown | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
253 | Sirti-WAN-R3-Ticket-231 | NA | 2026-05-05 | Aaqib | Optical module Temperature too High | High Temperature | AC working but not cooling | P009C3-ENC01-CE-01 |  |  | 25.22135257° 51.4353355° | Inside Doha | Critical | 2026-05-05 13:36 | 2026-05-05 13:43 | 6.85 | 2026-05-05 13:55 | 2026-05-05 16:27 | 151.55 | 170.55 | Alarm Auto restored before FLM reached the site however when FLM team reached the site they did overall inspection for the A/C system and rectified & adjusted the air conditioning settings and thermostat to ensure improved cooling performance. | Completed | Non-maintainer | Defect | N/a | Alarm Cleared | Khadar
254 | Sirti-WAN-R3-Ticket-232 | NA | 2026-05-05 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | SAL-ENC32-CE-01 |  |  | 25.1165799° 51.1812367° | Outside Doha | Critical | 2026-05-05 15:47 | 2026-05-05 15:51 | 3.8333 | 2026-05-05 15:51 | 2026-05-05 15:53 | 1.7167 | 5.55 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
255 | Sirti-WAN-R3-Ticket-233 | NA | 2026-05-05 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P023C3-ENC174-UPE-02 P023C3-ENC174-CE-01 |  |  | 25.0168866° 51.490473° | Outside Doha | Critical | 2026-05-05 18:49 | 2026-05-05 18:53 | 4 | 2026-05-05 18:53 | 2026-05-05 19:01 | 8.0667 | 12.0667 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
256 | Sirti-WAN-R3-Ticket-234 | NA | 2026-05-06 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | FLM Found RCCB tripped at ITS cabiet | P004-ENC43-CE-01 P004-ENC43-UPE-02 |  |  | 25.3374686° 51.3242872° | Outside Doha | Critical | 2026-05-06 07:29 | 2026-05-06 07:34 | 5 | 2026-05-06 07:40 | 2026-05-06 08:14 | 33.5667 | 44.5667 | FLM switched on tripped CB at cabinet side | Completed | Maintainer | N/a | N/a | Alarm Cleared | Hichem
257 | Sirti-WAN-R3-Ticket-235 | NA | 2026-05-06 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P023C2-ENC43-CE-01 |  |  | 25.1701761 51.3230788 | Outside Doha | Critical | 2026-05-06 07:29 | 2026-05-06 07:35 | 5.75 | 2026-05-06 07:35 | 2026-05-06 08:13 | 37.7667 | 43.5167 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Irshad
258 | Sirti-WAN-R3-Ticket-236 | NA | 2026-05-06 | AMR | Power Modules stopped working | Power Modules stopped working | FLM Checked the power at the cabinet and found that the UPS has no output. | SAL-ENC20-CE-01 |  |  | 25.1435454° 51.2478413° | Outside Doha | Critical | 2026-05-06 12:30 | 2026-05-06 12:35 | 5 | 2026-05-06 12:42 | 2026-05-06 13:35 | 53.15 | 65.15 | FLM performed a restart of the UPS. | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hichem
259 | Sirti-WAN-R3-Ticket-237 | NA | 2026-05-06 | AMR | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | SAL-ENC26-CE-01 |  |  | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-06 12:32 | 2026-05-06 12:37 | 5 | 2026-05-06 12:37 | 2026-05-06 13:34 | 57.3333 | 62.3333 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Najeeb
260 | Sirti-WAN-R3-Ticket-238 | NA | 2026-05-07 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity for UPS replacement | P006-ENC17-UPE-02 P006-ENC17-CE-01 |  |  | 25.19542° 51.454° | Inside Doha | Critical | 2026-05-07 02:32 | 2026-05-07 02:33 | 1 | 2026-05-07 02:36 | 2026-05-07 02:48 | 11.6 | 15.1667 | Planned activity for UPS replacement | Completed | Non-maintainer | 3rd Party | N/a | Devices Back Online | Ghulam
261 | Sirti-WAN-R3-Ticket-239 | NA | 2026-05-07 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity for UPS replacement | P006-ENC17-UPE-02 P006-ENC17-CE-01 |  |  | 25.19542° 51.454° | Inside Doha | Critical | 2026-05-07 03:15 | 2026-05-07 03:18 | 3 | 2026-05-07 03:19 | 2026-05-07 03:29 | 10.0833 | 14.0833 | Planned activity for UPS replacement | Completed | Non-maintainer | 3rd Party | N/a | Devices Back Online | Ghulam
262 | Sirti-WAN-R3-Ticket-240 | NA | 2026-05-07 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity for UPS replacement | P006-ENC17-UPE-02 P006-ENC17-CE-01 |  |  | 25.19542° 51.454° | Inside Doha | Critical | 2026-05-07 03:41 | 2026-05-07 03:43 | 2 | 2026-05-07 03:44 | 2026-05-07 03:55 | 10.2667 | 13.2667 | Planned activity for UPS replacement | Completed | Non-maintainer | 3rd Party | N/a | Devices Back Online | Ghulam
263 | Sirti-WAN-R3-Ticket-241 | NA | 2026-05-07 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | SAL-ENC09-CE-01 |  |  | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-05-07 09:32 | 2026-05-07 09:33 | 1 | 2026-05-07 09:33 | 2026-05-07 09:35 | 2 | 3 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
264 | Sirti-WAN-R3-Ticket-242 | NA | 2026-05-07 | Adel | CPU Temperature too high | High Temperature | Current temperature is 58°C at SFU board 6 | P008C3-ENC25-UPE-02 |  |  | 25.2341068° 51.50261° | Inside Doha | Critical | 2026-05-07 13:11 | 2026-05-07 13:13 | 2 | 2026-05-07 13:26 | 2026-05-07 14:38 | 72 | 87 | There is issue with AC and schema maintained by Salam Tech | Completed | Non-maintainer | 3rd Party | Salam Tech | Alarm Cleared | -
265 | Sirti-WAN-R3-Ticket-243 | NA | 2026-05-07 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | no Karomaa power at cabinet side | P007C1-ENC31-UPE-01 |  |  | 25.306727 51.411587 | Inside Doha | Critical | 2026-05-07 13:23 | 2026-05-07 13:25 | 2.1167 | 2026-05-07 14:35 | 2026-05-07 14:57 | 21.9 | 94.0167 | CB tripped at FP side due to a short circuit on A/C. Site restored after turning on CB | Completed | Non-maintainer | Defect | N/a | Devices Back Online | hicham
266 | Sirti-WAN-R3-Ticket-244 | NA | 2026-05-07 | Adel | Optical module temperature too high | High Temperature | High Temperature inside the Cabinet | 22FEB-ENC25-CE-01 |  |  | 25.31832397° 51.47088144° | Inside Doha | Critical | 2026-05-07 13:44 | 2026-05-07 13:46 | 2 | 2026-05-07 13:46 | 2026-05-07 14:54 | 67.8167 | 69.8167 | The compressor was not working. Then adjusted the AC function settings and temperature on the thermostat control system. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Sanjeewa
267 | Sirti-WAN-R3-Ticket-245 | NA | 2026-05-07 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | SAL-ENC09-CE-01 |  |  | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-05-07 13:50 | 2026-05-07 13:52 | 2 | 2026-05-07 13:52 | 2026-05-07 13:53 | 1 | 3 | Cheked the power cables & the voltage at the MCB, found a loose connection for the power cable at the terminal blocks | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Khadar
268 | Sirti-WAN-R3-Ticket-246 | NA | 2026-05-07 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity for fixing the power cables properly to the terminal blocks | SAL-ENC09-CE-01 |  |  | 25.2039088° 51.3945681° | Outside Doha | Critical | 2026-05-07 15:11 | 2026-05-07 15:18 | 7 | 2026-05-07 15:26 | 2026-05-07 15:41 | 15 | 30 | Disconnected the power cables from terminal blocks, replaced the cable lugs and reconnected and tightened the cables to the power terminal blocks | Completed | Non-maintainer | Planned Activity | N/a | Devices Back Online | Khadar
269 | Sirti-WAN-R3-Ticket-247 | NA | 2026-05-07 | Abubaker | Link down | Link Down | Found high Temp at the cabinet as A/C is not cooling properly | 22FEB-ENC25-CE-01 |  |  | 25.31832397° 51.47088144° | Inside Doha | Critical | 2026-05-07 15:45 | 2026-05-07 15:56 | 11 | 2026-05-07 15:56 | 2026-05-07 16:08 | 12 | 23 | Port went down during FLM troubleshooting the high Temp issue on site | Completed | Non-maintainer | Defect | N/a | Devices Back Online | Sanjeewa
270 | Sirti-WAN-R3-Ticket-248 | NA | 2026-05-08 | Sanket | Power Modules stopped working | Power Modules stopped working | The UPS has no output. | SAL-ENC20-CE-01 |  | Zone 82 | 25.1435454° 51.2478413° | Outside Doha | Critical | 2026-05-08 03:40 | 2026-05-08 03:43 | 3.1667 | 2026-05-08 04:20 | 2026-05-08 05:09 | 49.1667 | 89.3333 | FLM performed a restart of the UPS. | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Umair
271 | Sirti-WAN-R3-Ticket-249 | NA | 2026-05-08 | Sanket | Link down | LAN Link Down | While Trouble shooting of UPS issue, the link was down (GE 1/0/9) | SAL-ENC20-CE-01 |  | Zone 82 | 25.1435454° 51.2478413° | Outside Doha | Critical | 2026-05-08 04:31 | 2026-05-08 04:32 | 1.0167 | 2026-05-08 04:32 | 2026-05-08 04:33 | 0.46667 | 1.4833 | While Trouble shooting of UPS issue, The link is down towards LAN | Completed | Non-maintainer | 3rd Party | RMC | Alarm Cleared | Umair
272 | Sirti-WAN-R3-Ticket-250 | NA | 2026-05-08 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The power socket live cable has shorted, which caused the socket breaker to trip. The breaker tripped due to this fault | SAL-ENC45-CE-01 |  | Zone 83 | 25.005944° 51.042739° | Outside Doha | Critical | 2026-05-08 04:42 | 2026-05-08 04:47 | 5.0833 | 2026-05-08 06:00 | 2026-05-08 06:09 | 8.7167 | 86.8333 | Removed the shorted cable from the power socket, fixed the wiring properly, and reset the breaker. | Completed | Maintainer | N/a | N/a | Devices Back Online | Umair
273 | Sirti-WAN-R3-Ticket-251 | NA | 2026-05-08 | Sanket | Power Modules stopped working | Power Modules stopped working | UPS DB-03 Main breaker was tripped | DUK-DBR-UPE-01 DUK-DBR-USG-01 DUK-DBR-USG-02 |  |  | 25.2088874 51.4008611 | Outside Doha | Critical | 2026-05-08 06:37 | 2026-05-08 06:43 | 6 | 2026-05-08 07:28 | 2026-05-08 07:59 | 30.6 | 82.0667 | FLM switched on tripped main CB at UPS DB-03 | Completed | Non-maintainer | Defect | UPS | Devices Back Online | nageeb
274 | Sirti-WAN-R3-Ticket-252 | NA | 2026-05-08 | Adel | Link down | LAN Link Down | UPS DB-03 Main breaker was tripped | P004-MOQ-CE-01 |  |  | 25.319385 51.352255 | Outside Doha | Critical | 2026-05-08 06:37 | 2026-05-08 06:40 | 3 | 2026-05-08 07:35 | 2026-05-08 08:04 | 28.6833 | 87.1667 | FLM switched on tripped main CB at UPS DB-03 | Completed | Non-maintainer | Defect | UPS | Devices Back Online | irshad
275 | Sirti-WAN-R3-Ticket-253 | NA | 2026-05-08 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | CRR-ENC14-CE-01 |  |  | 25.26272 51.52569 | Inside Doha | Critical | 2026-05-08 21:05 | 2026-05-08 21:09 | 3.6667 | 2026-05-08 21:05 | 2026-05-08 21:27 | 21.7667 | 21.7667 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
276 | Sirti-WAN-R3-Ticket-254 | NA | 2026-05-08 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | CRR-ENC14-CE-01 |  |  | 25.26272 51.52569 | Inside Doha | Critical | 2026-05-08 21:40 | 2026-05-08 21:40 | 0.33333 | 2026-05-08 21:40 | 2026-05-08 22:01 | 21.7833 | 21.7833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
277 | Sirti-WAN-R3-Ticket-255 | NA | 2026-05-10 | Adel | CPU Temperature too high | High Temperature | AC CB was tripped and AC is not working | P007C2-ENC99-UPE-02 |  |  | 25.2967109° 51.4488814° | Inside Doha | Major | 2026-05-10 11:24 | 2026-05-10 11:26 | 2 | 2026-05-10 12:06 | 2026-05-10 14:17 | 130.6833 | 172.3333 | AC is now functioning properly after the following work was completed: installation of a new 250mm compressor fan, replacement of the PCB controller, repair of the single-phase dual motor evaporator fan, and fitting of both an 8 µF capacitor and a 35 µF capacitor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham
278 | Sirti-WAN-R3-Ticket-256 | NA | 2026-05-10 | Adel | Temperature higher than Upper threshold | High Temperature | High Temperature inside the Cabinet | P007C1-ENC31-UPE-01 |  |  | 25.298365 51.437959 | Inside Doha | Critical | 2026-05-10 13:15 | 2026-05-10 13:17 | 2 | 2026-05-10 13:30 | 2026-05-10 13:36 | 6.0833 | 20.7333 | AC1 is cooling well, and AC2 was serviced with a new SECOP SC15G compressor, capacitor, refrigerant refill, and thorough cleaning; after testing, both units are now working and cooling efficiently. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham
279 | Sirti-WAN-R3-Ticket-257 | NA | 2026-05-10 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P005-ENC414-CE-01 |  |  | 25.3335964° 51.4482522° | Outside Doha | Critical | 2026-05-10 15:08 | 2026-05-10 15:11 | 3 | 2026-05-10 15:12 | 2026-05-10 15:13 | 1.75 | 5.75 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
280 | Sirti-WAN-R3-Ticket-258 | NA | 2026-05-10 | Sanket | CPU Temperature too high | High Temperature | The capacitor (40Plus5) is faulty, and the fan unit is also faulty. | P007C2-ENC99-UPE-02 |  | Zone 54 | 25.2967109° 51.4488814° | Inside Doha | Major | 2026-05-10 15:32 | 2026-05-10 15:40 | 7.8167 | 2026-05-10 16:25 | 2026-05-10 16:31 | 5.6833 | 58.5 | AC is now operating smoothly after the following work was carried out: installation of a new 250mm compressor fan, replacement of the PCB controller, repair of the single-phase dual motor evaporator fan, and the addition of both an 8 µF capacitor and a 35 µF capacitor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
281 | Sirti-WAN-R3-Ticket-259 | NA | 2026-05-11 | Adel | Temperature higher than Upper threshold | High Temperature | Required: Nitrogen gas, vacuum cleaning, and R134a gas refill. | P023C1-ENC01-UPE-01 |  | Zone 90 | 25.111748° 51.583897° | Outside Doha | Critical | 2026-05-11 13:04 | 2026-05-11 13:06 | 2 | 2026-05-11 14:34 | 2026-05-11 14:38 | 4.1667 | 93.8667 | Attended site for AC cooling issue, carried out full inspection, replaced faulty compressor and related components, cleaned and flushed the system, recharged refrigerant, and tested successfully—unit now cooling properly, though sensor cable replacement is still pending and will be completed today. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
282 | Sirti-WAN-R3-Ticket-260 | NA | 2026-05-11 | Sanket | CPU Temperature too high | High Temperature | The capacitor (40Plus5) is faulty, and the fan unit is also faulty. | P007C2-ENC99-UPE-02 |  | Zone 54 | 25.2967109° 51.4488814° | Inside Doha | Critical | 2026-05-11 14:32 | 2026-05-11 14:42 | 9.6333 | 2026-05-11 15:25 | 2026-05-11 15:43 | 18.3667 | 71 | AC is now functioning as expected following the installation of a new 250mm compressor fan, replacement of the PCB controller, repair of the single-phase dual motor evaporator fan, and the addition of both an 8 µF capacitor and a 35 µF capacitor. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
283 | Sirti-WAN-R3-Ticket-261 | NA | 2026-05-11 | Sanket | CPU Temperature too high | High Temperature | High Temperature inside the Cabinet | CRR-ENC16-UPE-01 |  |  | 25.2590324° 51.537498° | Inside Doha | Major | 2026-05-11 15:49 | 2026-05-11 15:54 | 4.6 | 2026-05-11 15:55 | 2026-05-11 16:00 | 5.7333 | 11.3333 | Alarm Auto restored before FLM reached the site | Completed | Non-maintainer | Defect | AC | Alarm Cleared | -
284 | Sirti-WAN-R3-Ticket-262 | NA | 2026-05-11 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P010-ENC61-CE-01 |  |  | 25.1700975° 51.4699752° | Outside Doha | Critical | 2026-05-11 20:38 | 2026-05-11 20:42 | 4 | 2026-05-11 20:45 | 2026-05-11 20:47 | 1.2667 | 8.2667 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
285 | Sirti-WAN-R3-Ticket-263 | NA | 2026-05-11 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P010-ENC61-CE-01 |  |  | 25.1700975° 51.4699752° | Outside Doha | Critical | 2026-05-11 21:39 | 2026-05-11 21:41 | 2 | 2026-05-11 21:41 | 2026-05-11 21:44 | 3.2667 | 5.2667 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
286 | Sirti-WAN-R3-Ticket-264 | NA | 2026-05-11 | Sanket | Power Modules stopped working | Power Modules stopped working | CB was found tripped. 1 power module in DWDM is faulty | P012-ENC30-USG-01 P012_Pri |  |  | 25.2162349° 51.5021362° | Inside Doha | Critical | 2026-05-11 21:41 | 2026-05-11 21:49 | 7.15 | 2026-05-11 23:43 | 2026-05-12 | 17 | 138.55 | During the team’s visit, it was found that the AC breaker had tripped. After switching it back on, all modules were restored except one power module in the DWDM system. The FLM team confirmed that the power cable was receiving power, but when the module was swapped with another chassis, it still failed to operate. Based on these findings, the issue is suspected to be a faulty AC board that caused the breaker to trip. Not Sirti AC and Sirti team attended and made safe and left. Fault to be closed from Sirti side. | Completed | Non-maintainer | 3rd Party | Others | Devices Not affected | Umar and Hassan
287 | Sirti-WAN-R3-Ticket-265 | NA | 2026-05-11 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | 1 Power Supply found faulty | P010-ENC61-CE-01 |  | Zone 54 | 25.1700975° 51.4699752° | Outside Doha | Critical | 2026-05-11 23:39 | 2026-05-11 23:41 | 2.5833 | 2026-05-11 23:41 | 2026-05-11 23:50 | 8.5167 | 11.1 | Power supply replacement Done | Completed | Maintainer | N/a | N/a | Devices Back Online | Sarjoon
289 | Sirti-WAN-R3-Ticket-266 | NA | 2026-05-12 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Device went down during replacement of Power supply | P010-ENC61-CE-01 |  | Zone 54 | 25.1700975° 51.4699752° | Outside Doha | Critical | 2026-05-12 00:26 | 2026-05-12 00:28 | 2.2333 | 2026-05-12 00:28 | 2026-05-12 00:32 | 3.7 | 5.9333 | Power cables arrangement during the activity | Completed | Non-maintainer | Planned Activity | N/a | Devices Back Online | Sarjoon
288 | Sirti-WAN-R3-Ticket-267 | NA | 2026-05-12 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P014-Enc13-UPE-02 P014-Enc13-DSW13 |  |  | 25.257307° 51.549776° | Inside Doha | Critical | 2026-05-12 03:44 | 2026-05-12 03:45 | 1.65 | 2026-05-12 03:45 | 2026-05-12 03:48 | 3.1 | 4.75 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
290 | Sirti-WAN-R3-Ticket-268 | NA | 2026-05-12 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P014-Enc13-UPE-02 P014-Enc13-DSW13 |  |  | 25.257307° 51.549776° | Inside Doha | Critical | 2026-05-12 04:19 | 2026-05-12 04:22 | 3.25 | 2026-05-12 04:22 | 2026-05-12 04:24 | 1.5667 | 4.8167 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
291 | Sirti-WAN-R3-Ticket-269 | NA | 2026-05-12 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | SAL-ENC32-CE-01 |  |  | 25.1165799° 51.1812367° | Outside Doha | Critical | 2026-05-12 07:38 | 2026-05-12 07:40 | 2.15 | 2026-05-12 08:28 | 2026-05-12 10:02 | 93.7167 | 143.8667 | Kahramaa planned shutdown., FLM installed temporary PG to restore devices | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Najeeb
292 | Sirti-WAN-R3-Ticket-270 | NA | 2026-05-12 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | SAL-ENC32-CE-01 |  |  | 25.1165799° 51.1812367° | Outside Doha | Critical | 2026-05-12 12:13 | 2026-05-12 12:14 | 1 | 2026-05-12 12:14 | 2026-05-12 12:19 | 4.6667 | 5.6667 | FLM disconnected PG and Kahramma power is restored | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Najeeb
293 | Sirti-WAN-R3-Ticket-271 | NA | 2026-05-12 | Adel | CPU Temperature too high | High Temperature | AC is not cooling | CRR-ENC16-UPE-01 |  |  | 25.2590324° 51.537498° | Inside Doha | Critical | 2026-05-12 12:10 | 2026-05-12 12:14 | 4 | 2026-05-12 13:30 | 2026-05-12 13:33 | 2.8333 | 82.8333 | AC unit was inspected and power checked, with the leak repaired, gas refilled, and thorough cleaning performed; as a result, the AC is now cooling properly and operating in good condition | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Najeeb
294 | Sirti-WAN-R3-Ticket-272 | NA | 2026-05-12 | Adel | CPU Temperature too high | High Temperature | AC is not cooling | P010-ENC89-UPE-02 |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | Critical | 2026-05-12 14:01 | 2026-05-12 14:03 | 2 | 2026-05-12 14:08 | 2026-05-12 14:10 | 1.6667 | 8.6667 | Reset the AC function settings and temperature in the thermostat. Cleaned the AC control system with an air blower. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
295 | Sirti-WAN-R3-Ticket-273 | NA | 2026-05-12 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The FLM team is troubleshooting the AC issue | P007C2-ENC99-UPE-02 P007C2-ENC99-CE-01 |  | Zone 54 | 25.2967109° 51.4488814° | Inside Doha | Critical | 2026-05-12 15:09 | 2026-05-12 15:12 | 3 | 2026-05-12 15:12 | 2026-05-12 15:23 | 11.2833 | 14.2833 | During AC troubleshooting, the MCB was tripped OFF. After switching it ON, the device is now reachable | Completed | Non-maintainer | Defect | AC | Devices Back Online | Rizwan
296 | Sirti-WAN-R3-Ticket-274 | NA | 2026-05-12 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The FLM team is troubleshooting the AC issue | CRR-ENC16-UPE-01 CRR-ENC16-CE-01 |  |  | 25.2590324° 51.537498° | Inside Doha | Critical | 2026-05-12 18:49 | 2026-05-12 18:50 | 1 | 2026-05-12 18:51 | 2026-05-12 18:55 | 3.9167 | 5.9167 | During AC troubleshooting, the MCB was tripped OFF. After switching it ON, the device is now reachable | Completed | Non-maintainer | Defect | AC | Devices Back Online | Eric
297 | Sirti-WAN-R3-Ticket-275 | NA | 2026-05-12 | Sanket | Power Modules stopped working | Power Modules stopped working | Alarm Auto restored before FLM reached the site | SAL-ENC20-UPE-01 |  | Zone 82 | 25.1435454° 51.2478413° | Outside Doha | Critical | 2026-05-12 19:06 | 2026-05-12 19:10 | 3.6167 | 2026-05-12 19:11 | 2026-05-12 19:12 | 1.1167 | 5.7333 | Alarm Auto restored before FLM reached the site | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | -
298 | Sirti-WAN-R3-Ticket-276 | NA | 2026-05-13 | Aaqib | Link Down | LAN Link Down | Link connected to Access switch at tunnel | P005-TCR-CE-01 |  |  | 25.3199307 51.447548 | Outside Doha | Critical | 2026-05-13 01:07 | 2026-05-13 01:15 | 8.1667 | 2026-05-13 01:07 | 2026-05-13 01:44 | 37.3667 | 37.3667 | Link is connected to access Switch installed inside P005 tunnel and auto restored just before FLM reaching site | Completed | Non-maintainer | 3rd Party | N/a | Alarm Cleared | -
299 | Sirti-WAN-R3-Ticket-276 | NA | 2026-05-13 | Aaqib | Link Down | LAN Link Down | Link connected to Access switch at tunnel | P005-TCR-CE-02 |  |  | 25.3199307 51.447548 | Outside Doha | Critical | 2026-05-13 01:07 | 2026-05-13 01:15 | 8.1667 | 2026-05-13 01:07 | 2026-05-13 01:44 | 37.3833 | 37.3833 | Link is connected to access Switch installed inside P005 tunnel and auto restored just before FLM reaching site | Completed | Non-maintainer | 3rd Party | N/a | Alarm Cleared | -
300 | Sirti-WAN-R3-Ticket-277 | NA | 2026-05-13 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Device CB in PDU was found tripped inside cabinet | P023C3-ENC174-CE-01 |  |  | 25.0168866° 51.490473° | Outside Doha | Critical | 2026-05-13 05:21 | 2026-05-13 05:25 | 4.35 | 2026-05-13 05:52 | 2026-05-13 05:58 | 5.8333 | 37.4167 | Device restored after turning on CB in PDU | Completed | Maintainer | N/a | N/a | Alarm Cleared | Umair
301 | Sirti-WAN-R3-Ticket-278 | NA | 2026-05-13 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | 22FEB-ENC13-CE-01 |  |  | 25.27506948° 51.48993629° | Inside Doha | Critical | 2026-05-13 06:18 | 2026-05-13 06:20 | 2.0667 | 2026-05-13 06:20 | 2026-05-13 06:24 | 3.8833 | 5.95 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
302 | Sirti-WAN-R3-Ticket-279 | NA | 2026-05-13 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | AC CB is tripped (short-circuit) and tripping other devices CBs | P023C3-ENC174-UPE-02 P023C3-ENC174-CE-01 |  |  | 25.0168866° 51.490473° | Outside Doha | Critical | 2026-05-13 09:08 | 2026-05-13 09:10 | 2 | 2026-05-13 10:03 | 2026-05-13 11:01 | 57.6 | 112.2333 | FLM switched off defected AC to restore the switches | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham
303 | Sirti-WAN-R3-Ticket-280 | NA | 2026-05-13 | Adel | CPU Temperature too high | High Temperature | Compressor high Amp and overheating, | P007C2-ENC99-UPE-02 |  | Zone 54 | 25.2967109° 51.4488814° | Inside Doha | Critical | 2026-05-13 13:17 | 2026-05-13 13:19 | 2 | 2026-05-13 13:51 | 2026-05-13 13:54 | 2.6667 | 36.6667 | At site P007C2-ENC99-UPE-02, the faulty compressor was replaced and the system serviced, but cooling failed as the new compressor overheated and tripped despite other components testing normal; abnormal performance was confirmed under load, so the unit was removed, returned, and a replacement collected, with further work handed over to the next shift. We installed a new AC compressor, checked the fan connections, and refilled the refrigerant gas. After testing, the unit is now operating properly with strong cooling performance | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan
304 | Sirti-WAN-R3-Ticket-281 | NA | 2026-05-13 | Adel | Temperature higher than Upper threshold | High Temperature | Capacitor and Compressor is faulty | P007C5P1-ENC06-UPE-02 |  |  | 25.2694167° 51.4767778° | Inside Doha | Critical | 2026-05-13 13:27 | 2026-05-13 13:29 | 2 | 2026-05-13 14:16 | 2026-05-13 14:18 | 2 | 50.9833 | Leak repaired, gas refilled, compressor replaced, and full cleaning completed and AC is working normally | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
305 | Sirti-WAN-R3-Ticket-282 | NA | 2026-05-13 | Adel | CPU Temperature too high | High Temperature | AC compressor is not functioning | P010-ENC89-UPE-02 |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | Critical | 2026-05-13 13:34 | 2026-05-13 13:37 | 3 | 2026-05-13 14:42 | 2026-05-13 14:59 | 17.15 | 85.3667 | Check the cabinet AC compressor to confirm it is not functioning. Then verify the AC status, power supply, and voltage. After that, turn off the AC power and restart the system. Once restarted, the physical AC unit operates normally, and all components are running properly. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
306 | Sirti-WAN-R3-Ticket-283 | NA | 2026-05-13 | Adel | CPU Temperature too high | High Temperature | AC is not cooling | P010-ENC01-UPE01 |  | Zone 81 | 25.1398815° 51.4073931° | Outside Doha | Critical | 2026-05-13 14:30 | 2026-05-13 14:32 | 2 | 2026-05-13 14:45 | 2026-05-13 14:46 | 1 | 16.8333 | Checked cabinet AC compressor — not working. Verified power and voltage. Restarted AC power, adjusted settings and thermostat. Compressor is now running. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
307 | Sirti-WAN-R3-Ticket-284 | NA | 2026-05-13 | Sanket | Power Modules stopped working | Power Modules stopped working | UPS DB-03 Main breaker was tripped at DUK-DBR | DUK-DBR-UPE-01 DUK-DBR-USG-01 DUK-DBR-USG-02 |  | Zone 80 | 25.3775425 51.22843816 | Outside Doha | Critical | 2026-05-13 19:16 | 2026-05-13 19:19 | 3.2667 | 2026-05-13 20:25 | 2026-05-13 20:42 | 16.25 | 85.5167 | FLM switched on tripped main CB at UPS DB-03 at DUK-DBR | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hassan
308 | Sirti-WAN-R3-Ticket-284 | NA | 2026-05-13 | Sanket | Link down | LAN Link Down | UPS DB-03 Main breaker was tripped at DUK-DBR | P004-MOQ-CE-01 DUK-DBR-USG-01 DUK-DBR-USG-02 |  |  | 25.319385 51.352255 | Outside Doha | Critical | 2026-05-13 19:16 | 2026-05-13 19:20 | 4.1 | 2026-05-13 20:25 | 2026-05-13 20:47 | 21.45 | 90.7667 | FLM switched on tripped main CB at UPS DB-03 at DUK-DBR | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hassan
309 | Sirti-WAN-R3-Ticket-285 | NA | 2026-05-13 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P012-ENC101-CE-01 |  |  | 25.1957136° 51.4525682° | Inside Doha | Critical | 2026-05-13 20:37 | 2026-05-13 20:39 | 2 | 2026-05-13 20:40 | 2026-05-13 20:41 | 1.4167 | 4.0833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
310 | Sirti-WAN-R3-Ticket-286 | NA | 2026-05-13 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | During ASW-ENC99 (LAN) troubleshooting, the MCB was tripped OFF. After switching it ON, the device is now reachable | P012-ENC101-CE-01 |  |  | 25.1957136° 51.4525682° | Inside Doha | Critical | 2026-05-13 22:04 | 2026-05-13 22:06 | 2 | 2026-05-13 22:10 | 2026-05-13 22:11 | 1.3333 | 7 | During ASW-ENC99 (LAN) troubleshooting, the MCB was tripped OFF. After switching it ON, the device is now reachable | Completed | Non-maintainer | Planned Activity | N/a | Devices Back Online | Masthanbasha
311 | Sirti-WAN-R3-Ticket-287 | NA | 2026-05-13 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P006-ENC17-UPE-02 P006-ENC17-CE-01 |  |  | 25.19542° 51.454 | Inside Doha | Critical | 2026-05-13 22:08 | 2026-05-13 22:11 | 3 | 2026-05-13 22:12 | 2026-05-13 22:13 | 1.0833 | 5.2833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
312 | Sirti-WAN-R3-Ticket-287 | NA | 2026-05-13 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P006-ENC02-UPE-01 P006-ENC02-CE-01 |  |  | 25.2190399° 51.4369501° | Inside Doha | Critical | 2026-05-13 22:21 | 2026-05-13 22:24 | 3 | 2026-05-13 22:25 | 2026-05-13 22:26 | 0.78333 | 4.95 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
313 | Sirti-WAN-R3-Ticket-288 | NA | 2026-05-14 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Planned UPS replacement activity | P010-ENC61-CE-01 |  |  | 25.1700975° 51.4699752° | Outside Doha | Critical | 2026-05-14 01:26 | 2026-05-14 01:28 | 2.4667 | 2026-05-14 01:28 | 2026-05-14 01:34 | 5.65 | 8.1167 | Planned UPS replacement activity | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Ghulam
314 | Sirti-WAN-R3-Ticket-289 | NA | 2026-05-14 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Planned UPS replacement activity | P010-ENC61-CE-01 |  |  | 25.1700975° 51.4699752° | Outside Doha | Critical | 2026-05-14 04:57 | 2026-05-14 05:02 | 5 | 2026-05-14 05:02 | 2026-05-14 05:09 | 7 | 12 | Planned UPS replacement activity | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Ghulam
315 | Sirti-WAN-R3-Ticket-290 | NA | 2026-05-14 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | Kahramaa planned shutdown | P029C2-ENC05-CE-01 |  |  | 25.281278° 51.503972° | Inside Doha | Critical | 2026-05-14 08:00 | 2026-05-14 08:03 | 3 | 2026-05-14 08:17 | 2026-05-14 09:46 | 89.1 | 106.25 | Kahramaa planned shutdown, FLM installed temporary PG to restore devices | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Hicham
316 | Sirti-WAN-R3-Ticket-291 | NA | 2026-05-14 | Adel | Power Modules stopped working | power alarm | UPS DB-03 Main breaker was tripped at DUK-DBR | DUK-DBR-UPE-01 DUK-DBR-USG-01 DUK-DBR-USG-02 |  |  | 25°22'39.2"N 51°13'42.0"E | Outside Doha | Critical | 2026-05-14 09:55 | 2026-05-14 09:59 | 3.95 | 2026-05-14 10:40 | 2026-05-14 10:42 | 2.2833 | 47.2333 | FLM switched on tripped main CB at UPS DB-03 at DUK-DBR | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hicham
317 | Sirti-WAN-R3-Ticket-291 | NA | 2026-05-14 | Adel | link down | LAN Link Down | UPS DB-03 Main breaker was tripped at DUK-DBR | P004-MOQ-CE-01 |  |  | 25°22'39.2"N 51°13'42.0"E | Outside Doha | Critical | 2026-05-14 09:55 | 2026-05-14 09:59 | 4.0167 | 2026-05-14 10:40 | 2026-05-14 10:47 | 6.9833 | 52 | FLM switched on tripped main CB at UPS DB-03 at DUK-DBR | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hicham
318 | Sirti-WAN-R3-Ticket-292 | NA | 2026-05-14 | Adel | system power lower than the threshold | End device power alarm | ADAM6060 module is not communication properly which is connected to port 1/2 | P005-ENC412-CE-01 |  |  | 25.3203266° 51.4472961° | Outside Doha | Critical | 2026-05-14 09:40 | 2026-05-14 09:42 | 2.0667 | 2026-05-14 10:30 | 2026-05-14 10:35 | 5 | 55.0667 | No fault detected from WAN/switch side. Investigation confirmed the alarm is related to the ADAM-6060 module connected on Gi1/2, which showed repeated PoE detect/disconnect events and is currently offline with no MAC address or LLDP neighbor detected. Switch PSU and environmental status are healthy. Also, the ADAM-6060 module is externally powered, therefore no fault has been identified from WAN/switch side. | Completed | Non-maintainer | 3rd party | 3rd party | Alarm Cleared | Hicham
319 | Sirti-WAN-R3-Ticket-293 | NA | 2026-05-14 | Sanket | CPU Temperature too high | High Temperature | AC is not cooling | P010-ENC01-UPE01 |  | Zone 81 | 25.1398815° 51.4073931° | Outside Doha | Critical | 2026-05-14 15:58 | 2026-05-14 16:04 | 6.1667 | 2026-05-14 16:06 | 2026-05-14 16:08 | 1.6667 | 9.8333 | Alarm Auto restored before FLM reached the site | Completed | Non-maintainer | Defect | AC | Alarm Cleared | -
320 | Sirti-WAN-R3-Ticket-294 | NA | 2026-05-14 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kahramaa planned shutdown | P029C2-ENC05-CE-01 |  | Zone 38 | 25.281278° 51.503972° | Inside Doha | Critical | 2026-05-14 16:38 | 2026-05-14 16:40 | 2.3333 | 2026-05-14 16:41 | 2026-05-14 17:04 | 22.1 | 25.4333 | Kahramaa planned shutdown, FLM switched temporary PG to Kahramaa | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | Salem Haj
321 | Sirti-WAN-R3-Ticket-295 | NA | 2026-05-14 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P006-ENC02-UPE-01 P006-ENC02-CE-01 |  |  | 25.2190399° 51.4369501° | Inside Doha | Critical | 2026-05-14 18:03 | 2026-05-14 18:05 | 2 | 2026-05-14 18:07 | 2026-05-14 18:08 | 1.1667 | 5 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
322 | Sirti-WAN-R3-Ticket-296 | NA | 2026-05-15 | Adel | link down | LAN Link Down | no power at LAN cabinet ENC07 | P023C1-ENC01-CE-01 |  |  | 25.111748° 51.583897° | Outside Doha | Critical | 2026-05-15 10:03 | 2026-05-15 10:07 | 4 | 2026-05-15 10:50 | 2026-05-15 13:46 | 175.95 | 222.5167 | FLM switchon on CB at LAN ENC07 | Completed | Non-maintainer | N/a | N/a | Alarm Cleared | Najeeb
323 | Sirti-WAN-R3-Ticket-297 | NA | 2026-05-15 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P012-ENC82-CE-01 |  |  | 25.1917451° 51.4552041 | Inside Doha | Critical | 2026-05-15 15:13 | 2026-05-15 15:18 | 5.15 | 2026-05-15 15:20 | 2026-05-15 15:21 | 0.91667 | 8.1167 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
324 | Sirti-WAN-R3-Ticket-297 | NA | 2026-05-15 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P006-ENC17-UPE-02 P006-ENC17-CE-01 |  |  | 25.19542° 51.454° | Inside Doha | Critical | 2026-05-15 23:17 | 2026-05-15 23:22 | 5.1 | 2026-05-15 23:22 | 2026-05-15 23:23 | 1.4833 | 6.5833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
325 | Sirti-WAN-R3-Ticket-298 | NA | 2026-05-16 | Abubaker | Link Down | WAN Link Down | QNBN Planned Activity | 22FEB-ENC25-UPE-02 (100GE 1/0/1) 22FEB-ENC01-UPE-01 (100GE 1/0/1) P003-TCR-NPE-01 (100GE 1/3/0/5) P003-TCR-NPE-01 (100GE 2/3/0/5) DWDM Links Down (P003_To_RMC_S P060_Pri P003_To_RMC_P SOC_P003-P015 Pri RMC_TO_P060_TO_RAA_S P060_Sec RMC_TO_P003_S_TO_P015_S SOC_TO_P060_RAA_Pri) |  | Lusail Expressway 22nd February Street | 25.31832397° 51.47088144° 25.2453756° 51.5148756° 25.3730597 51.5247872 | Inside Doha | Critical | 2026-05-16 01:01 | 2026-05-16 01:06 | 5.1667 | 2026-05-16 01:06 | 2026-05-16 04:39 | 213.3167 | 218.4833 | Planned QNBN Activity | Completed | Non-maintainer | 3rd Party | QNBN | Alarm Cleared | -
326 | Sirti-WAN-R3-Ticket-299 | NA | 2026-05-16 | Adel | Temperature higher than Upper threshold | High Temperature | AC02 compressor is found faulty | DUK-ENC12-UPE-02 |  | Zone 80 | 25.4302156° 51.1497491° | Outside Doha | Critical | 2026-05-16 12:12 | 2026-05-16 12:14 | 2 | 2026-05-16 15:28 | 2026-05-16 15:30 | 2.5833 | 198.3833 | AC2, the old compressor was removed, condenser and evaporator flushed with nitrogen, cleaned with a vacuum pump, a new 80Ufd capacitor installed, 134A gas refilled, temperature set, and parts cleaned. | Completed | Non-maintainer | Defect | AC | Alarm Cleared
327 | Sirti-WAN-R3-Ticket-300 | NA | 2026-05-16 | Adel | Temperature higher than Upper threshold | High Temperature | Gas leakage and Compressor power cable found faulty | P019-ENC15-UPE-01 |  | Zone 55 | 25.442833° 51.223831° | Inside Doha | Critical | 2026-05-16 12:01 | 2026-05-16 12:05 | 4 | 2026-05-16 12:21 | 2026-05-16 13:22 | 61.2667 | 81.0167 | Faulty power cable on the compressor was identified and replaced; additionally, a leak was fixed and thorough cleaning was carried out. | Completed | Non-maintainer | Defect | AC | Alarm Cleared
328 | Sirti-WAN-R3-Ticket-301 | NA | 2026-05-16 | Adel | Link down | LAN Link Down | link auto restored | RAA-ENC01-CE-01 |  |  | 25.284123° 51.5558539° | Inside Doha | Critical | 2026-05-16 12:32 | 2026-05-16 12:36 | 4 | 2026-05-16 12:36 | 2026-05-16 12:42 | 5.9833 | 9.9833 | Kahramaa power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
329 | Sirti-WAN-R3-Ticket-302 | NA | 2026-05-16 | Adel | Link down | LAN Link Down | link auto restored | SAL-ENC20-CE-01 |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-16 13:49 | 2026-05-16 13:50 | 1 | 2026-05-16 13:50 | 2026-05-16 13:51 | 1.0833 | 2.0833 | Kahramaa power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
330 | Sirti-WAN-R3-Ticket-303 | NA | 2026-05-16 | Adel | Temperature higher than Upper threshold | High Temperature | The A/C comperessor is not working properly | P010-ENC01-UPE01 |  | Zone 81 | 25.1398815° 51.4073931° | Outside Doha | Critical | 2026-05-16 14:24 | 2026-05-16 14:26 | 2 | 2026-05-16 15:01 | 2026-05-16 15:06 | 4.7833 | 41.5167 | Adjusted the temperature setting to 30°C; compressor started operating and cooling resumed. Checked compressor load and found it slightly high, then adjusted the refrigerant gas pressure accordingly. Monitored system operation and confirmed the compressor is now functioning properly. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric / Ghulam
331 | Sirti-WAN-R3-Ticket-304 | NA | 2026-05-16 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-16 15:28 | 2026-05-16 15:30 | 2.6667 | 2026-05-16 15:30 | 2026-05-16 15:35 | 5.0167 | 7.6833 | Kahramaa power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
332 | Sirti-WAN-R3-Ticket-305 | NA | 2026-05-16 | Aaqib | Power Modules stopped working | Power alarm | No Output from UPS | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-16 15:32 | 2026-05-16 15:35 | 3.2 | 2026-05-16 16:00 | 2026-05-16 16:17 | 17.1667 | 45.1833 | No output observed. UPS control settings checked and turned it ON. Alarm cleared | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Hassan
333 | Sirti-WAN-R3-Ticket-306 | NA | 2026-05-16 | Adel | Temperature higher than Upper threshold | High Temperature | A/C is not cooling | P010-ENC89-UPE-02 |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | Critical | 2026-05-16 13:27 | 2026-05-16 13:34 | 6.6833 | 2026-05-16 13:34 | 2026-05-16 13:56 | 21.8167 | 28.5 | Checked AC power supply, voltage, and compressor operation. Compressor was overheating and drawing high current (13A instead of normal 6–7A), confirming compressor failure. Removed faulty compressor and cleaned/flushed condenser and evaporator with nitrogen gas. Performed vacuum cleaning, refilled R22 gas, adjusted temperature settings, and cleaned AC components. Tested unit after servicing; AC cooling performance was restored and operating normally. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
334 | Sirti-WAN-R3-Ticket-307 | NA | 2026-05-17 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | No power found in Cabinet and FP from Khahrama side | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-17 15:47 | 2026-05-17 15:49 | 2.6 | 2026-05-17 16:37 | 2026-05-17 17:47 | 69.65 | 120.3333 | No power in FP, Kharama ticket (Refernece # 261100022460) is created after which power restored. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | khadar
335 | Sirti-WAN-R3-Ticket-308 | NA | 2026-05-17 | Aaqib | Power Modules stopped working | Power alarm | No Output from UPS | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-17 17:50 | 2026-05-17 17:51 | 1.7833 | 2026-05-17 17:51 | 2026-05-17 19:29 | 97.5667 | 99.35 | No Output from UPS. Power modules restored after Bypassing UPS | Completed | Non-maintainer | Defect | UPS | Alarm Cleared | Maasthan/khadar
336 | Sirti-WAN-R3-Ticket-309 | NA | 2026-05-17 | Aaqib | Link down | LAN Link Down | No power found in LAN Cabinet and FP from Khahrama side | SAL-ENC20-CE-01 |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-17 15:50 | 2026-05-17 15:51 | 1.5333 | 2026-05-17 17:52 | 2026-05-17 17:56 | 4 | 126.0667 | No power in FP at LAN side, Kharama ticket was created after which power restored. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | khadar
337 | Sirti-WAN-R3-Ticket-310 | NA | 2026-05-17 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | UPS Planned Bypassing Activity | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-17 18:47 | 2026-05-17 18:49 | 2.0333 | 2026-05-17 18:49 | 2026-05-17 19:04 | 14.5667 | 16.6 | Devices were down for bypassing UPS inside cabinet | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Maasthan/khadar
338 | Sirti-WAN-R3-Ticket-311 | NA | 2026-05-17 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | UPS Planned Bypassing Activity | SAL-ENC20-UPE-01 SAL-ENC20-CE-01 |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-17 19:38 | 2026-05-17 19:39 | 0.98333 | 2026-05-17 19:39 | 2026-05-17 19:43 | 4.5167 | 5.5 | Devices were down during bypassing UPS inside cabinet and troubleshooting CE power issue. | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Maasthan/khadar
339 | Sirti-WAN-R3-Ticket-312 | NA | 2026-05-17 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | UPS Planned Bypassing Activity | SAL-ENC20-CE-01 |  | Zone 82 | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-17 19:43 | 2026-05-17 19:43 | 0 | 2026-05-17 19:43 | 2026-05-17 19:46 | 3.0667 | 3.0667 | Devices were down during UPS bypassing and troubleshooting CE power issue. | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Maasthan/khadar
340 | Sirti-WAN-R3-Ticket-313 | NA | 2026-05-18 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P015-ENC80A-CE-01 |  | Zone 90 | 25.113315° 51.5735937° | Inside Doha | Critical | 2026-05-18 07:52 | 2026-05-18 07:53 | 1 | 2026-05-18 07:53 | 2026-05-18 07:54 | 1.3667 | 2.3667 | Kahramaa power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
341 | Sirti-WAN-R3-Ticket-314 | NA | 2026-05-18 | Sanket | Link down | LAN Link Down | The link is down towards Local Node (LAN) | DUK-ENC12-CE-01 |  | Zone 80 | 25.4302156° 51.1497491° | Outside Doha | Critical | 2026-05-18 11:32 | 2026-05-18 11:34 | 2 | 2026-05-18 12:26 | 2026-05-18 12:41 | 15 | 68.85 | The Link is down towards LAN | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Irshad
342 | Sirti-WAN-R3-Ticket-315 | NA | 2026-05-18 | Aaqib | Temperature higher than Upper threshold | High Temperature | AC02 compressor is found faulty | DUK-ENC12-UPE-02 |  | Zone 80 | 25.4302156° 51.1497491° | Outside Doha | Critical | 2026-05-18 12:38 | 2026-05-18 12:40 | 2.2167 | 2026-05-18 13:18 | 2026-05-18 13:43 | 25 | 65 | The AC breaker tripped because the compressor was faulty. We removed the old compressor and installed a new one. The condenser and evaporator were flushed with nitrogen and vacuumed. A new 80µF capacitor was fitted, R134a refrigerant was filled, and the thermostat temperature was set. Finally, all AC parts were cleaned with a blower and cloth. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | khadar
343 | Sirti-WAN-R3-Ticket-316 | NA | 2026-05-19 | Sanket | Link down | LAN Link Down (25GE 1/0/2) | KAHRAMAA Maintenance activity | SAL-ENC26-CE-01 |  | Zone 82 | 25.1435454° 51.2478413° | Outside Doha | Critical | 2026-05-19 07:02 | 2026-05-19 07:07 | 5 | 2026-05-19 07:52 | 2026-05-19 09:42 | 109.6 | 159.1667 | KAHRAMAA Maintenance activity, FLM installed temporary PG to restore devices | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Rizwan
344 | Sirti-WAN-R3-Ticket-317 | NA | 2026-05-19 | Sanket | Link down | LAN Link Down (25GE 1/0/3) | KAHRAMAA Maintenance activity | SAL-ENC26-CE-01 |  | Zone 82 | 25.1435454° 51.2478413° | Outside Doha | Critical | 2026-05-19 07:02 | 2026-05-19 07:07 | 5 | 2026-05-19 07:52 | 2026-05-19 10:59 | 186.6167 | 236.1833 | KAHRAMAA Maintenance activity | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | Rizwan
345 | Sirti-WAN-R3-Ticket-318 | NA | 2026-05-19 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Planned activity for Power Bypass | P015-ENC80A-CE-01 |  | Zone 90 | 25.113315° 51.5735937° | Inside Doha | Critical | 2026-05-19 12:23 | 2026-05-19 12:24 | 1 | 2026-05-19 12:28 | 2026-05-19 12:29 | 1 | 6.6 | Planned activity for Power Bypass | Completed | Non-maintainer | N/a | N/a | Devices Back Online | Najeeb
346 | Sirti-WAN-R3-Ticket-319 | NA | 2026-05-20 | Abubaker | Link down | LAN Link Down (GE 0/0/3) | LAN switch 1705-SR1-ASW-WI3-01 was not responding | P003-ENC05-CE-01-DGME01 |  | Zone 66 | 25.3811922° 51.5208128° | Inside Doha | Critical | 2026-05-20 01:01 | 2026-05-20 01:11 | 10.4 | 2026-05-20 01:52 | 2026-05-20 02:03 | 10.6167 | 62.1667 | FLM restarted the LAN switch 1705-SR1-ASW-WI3-01 connected to the port GE0/0/3 as the LAN switch was not responding | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Umair
347 | Sirti-WAN-R3-Ticket-320 | NA | 2026-05-20 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | P007C2-ENC99-CE-01 |  | Zone 54 | 25.2967109° 51.4488814° | Inside Doha | Critical | 2026-05-20 04:28 | 2026-05-20 04:32 | 4.1667 | 2026-05-20 04:32 | 2026-05-20 04:33 | 0.75 | 4.9167 | Kahramaa power interruption, the power & device restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Back Online | -
348 | Sirti-WAN-R3-Ticket-321 | NA | 2026-05-20 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | AC breaker was Tripped | P011-ENC55-CE-01 |  | Zone 49 | 25.2209722° 51.5862222° | Inside Doha | Critical | 2026-05-20 07:19 | 2026-05-20 07:22 | 3.1167 | 2026-05-20 08:05 | 2026-05-20 08:13 | 7.95 | 54.1167 | The AC breaker was found in a tripped state. Each time it was switched ON, it immediately tripped again. As a precaution, the AC unit has been isolated and temporarily kept OFF | Completed | Non-maintainer | Defect | AC | Device Back Online | Rizwan
349 | Sirti-WAN-R3-Ticket-322 | NA | 2026-05-20 | Sanket | CRC Error | LAN CRC Error Port GE 1/0/9 | The Ethernet cable has issue | SAL-ENC20-CE-01 |  | Zone 81 | 25.164986° 51.3063942° | Outside Doha | Critical | 2026-05-20 09:02 | 2026-05-20 09:05 | 3.3833 | 2026-05-20 09:36 | 2026-05-20 09:47 | 11.0167 | 45.1833 | The Ethernet cable has been replaced | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Hichem
350 | Sirti-WAN-R3-Ticket-323 | NA | 2026-05-20 | Sanket | CRC Error | WAN CRC Error Port 40GE 1/1/0/0 | SFP Issue | RMC-ENC-SSW-02 |  |  | 25.2410344° 51.4752267° | Inside Doha | Critical | 2026-05-20 11:35 | 2026-05-20 11:37 | 2 | 2026-05-20 11:40 | 2026-05-20 12:57 | 77.3667 | 81.75 | SFP module replaced at RMC-ENC-SSW-02, port 40GE 1/1/0/0 | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Arfa
351 | Sirti-WAN-R3-Ticket-324 | NA | 2026-05-21 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | ITS FP breaker tripped (Cable Burn) | P028C2-ENC01-CE-01 |  | Zone 27 | 25.2839108° 51.5496128° | Inside Doha | Critical | 2026-05-21 07:20 | 2026-05-21 07:25 | 4.5 | 2026-05-21 07:54 | 2026-05-21 08:25 | 31.3667 | 64.85 | The ITS feeder pillar main breaker was tripping repeatedly. When the FLM attempted to switch it ON, it turned OFF immediately. A temporary PG was installed to restore the devices. Further inspection of the ITS feeder pillar main cable identified a burnt section causing the short circuit and breaker tripping. The damaged cable section was removed, re-terminated with proper lugs, and reconnected to the breaker. | Completed | Maintainer | N/a | N/a | Device Back Online | Rizwan
352 | Sirti-WAN-R3-Ticket-325 | NA | 2026-05-21 | Sanket | Link Down | WAN link down (100GE 1/0/0 and 100GE 1/0/1) | Attenuator issues | RAA-ENC01-UPE-01 |  | Zone 48 | 25.284123° 51.5558539° | Inside Doha | Critical | 2026-05-21 07:07 | 2026-05-21 07:16 | 8.65 | 2026-05-21 07:48 | 2026-05-21 08:27 | 39.2167 | 80.1333 | The attenuators in the link were faulty. We replaced them and added new 5dB attenuators. The links are now restored. | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | Hichem
353 | Sirti-WAN-R3-Ticket-326 | NA | 2026-05-21 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | The ROMD inspection (Ashghal Team) | P040-CPE01-ENC01-DSW |  | Zone 48 | 25.284123° 51.5558539° | Inside Doha | Critical | 2026-05-21 07:07 | 2026-05-21 07:16 | 8.65 | 2026-05-21 07:48 | 2026-05-21 09:31 | 102.9333 | 143.85 | The ROMD inspection (Ashghal Team) | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Device Back Online | -
354 | Sirti-WAN-R3-Ticket-327 | NA | 2026-05-21 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | ITS FP breaker tripped (Cable Burn) | P028C2-ENC01-CE-01 |  | Zone 48 | 25.284123° 51.5558539° | Inside Doha | Critical | 2026-05-21 09:48 | 2026-05-21 09:49 | 1 | 2026-05-21 09:49 | 2026-05-21 09:53 | 3.6333 | 4.6333 | The ITS feeder pillar main breaker was tripping repeatedly. When the FLM attempted to switch it ON, it turned OFF immediately. A temporary PG was installed to restore the devices. Further inspection of the ITS feeder pillar main cable identified a burnt section causing the short circuit and breaker tripping. The damaged cable section was removed, re-terminated with proper lugs, and reconnected to the breaker. | Completed | Maintainer | N/a | N/a | Device Back Online | Rizwan
355 | Sirti-WAN-R3-Ticket-328 | NA | 2026-05-21 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | KAHRAMAA power interruption | CRR-ENC26-CE-01 |  | Zone 25 | 25.2675° 51.5259° | Inside Doha | Critical | 2026-05-21 10:08 | 2026-05-21 10:10 | 2.5 | 2026-05-21 10:41 | 2026-05-21 10:42 | 1.3833 | 34.4333 | Kahramaa power interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Back Online | Rizwan
356 | Sirti-WAN-R3-Ticket-329 | NA | 2026-05-21 | Sanket | Temperature higher than Upper threshold | High Temperature | AC is not cooling | P002-ENC14-UPE-02 |  | Zone 55 | 25.249° 51.471° | Inside Doha | Critical | 2026-05-21 11:47 | 2026-05-21 11:51 | 4.7 | 2026-05-21 12:17 | 2026-05-21 12:19 | 1.9333 | 32.2167 | Replaced the faulty 40+5 µF dual run capacitor and copper filter drier, and repaired the refrigerant leak at the compressor line. The AC unit was thoroughly cleaned and tested after completion of the work. Cooling performance is now normal, and the AC system is operating properly. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hichem
357 | Sirti-WAN-R3-Ticket-330 | NA | 2026-05-21 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | While Trouble shooting the AC issue , CB is tripped | P002-ENC14-UPE-02 P002-ENC14-CE-01 |  | Zone 55 | 25.249° 51.471° | Inside Doha | Critical | 2026-05-21 13:07 | 2026-05-21 13:08 | 1.1 | 2026-05-21 13:10 | 2026-05-21 13:13 | 3 | 6.1 | While Trouble shooting the AC issue , CB is tripped | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Rizwan
358 | Sirti-WAN-R3-Ticket-331 | NA | 2026-05-21 | Aaqib | Link Down | LAN Link down | Link Flapping and high ping delay/ intermittent due to cable bend | DUK-ENC06-CE-01 |  | Zone 80 | 25.3954062° 51.1985851° | Outside Doha | Critical | 2026-05-21 16:14 | 2026-05-21 16:25 | 10.35 | 2026-05-21 18:14 | 2026-05-21 18:19 | 5.2667 | 124.35 | Cable was forn bend and tight, Issue resolve after rerouting UTP cable. | Completed | Non-maintainer | Node Up | N/a | Alarm Cleared | AbuTahir
359 | Sirti-WAN-R3-Ticket-332 | NA | 2026-05-22 | Abubaker | Link Down | LAN Link down | The links P005-TCR-CE-01 (GE 1/0/13) P005-TCR-CE-02 (GE 1/0/13) were down from tunnel access switch side | P005-TCR-CE-01 P005-TCR-CE-02 |  |  | 25.3199307° 51.447548° | Outside Doha | Critical | 2026-05-22 02:38 | 2026-05-22 02:48 | 9.6167 | 2026-05-22 02:48 | 2026-05-22 06:03 | 194.8 | 204.4167 | Issue has been escalated to the tunnel team and they confirmed that the Linkshare down due to some fiber troubleshooting activity by tunnel team, Links restored after activity completed | Completed | Non-maintainer | 3rd Party | Tunnel Control Room Team (P005) | Alarm Cleared | -
360 | Sirti-WAN-R3-Ticket-333 | NA | 2026-05-22 | Sanket | Power Modules stopped working | Power Modules stopped working | PWR1 stopped working | P011-ENC44-UPE-02 |  |  | 25.223 51.58 | Inside Doha | Critical | 2026-05-22 09:29 | 2026-05-22 09:32 | 3.5333 | 2026-05-22 09:48 | 2026-05-22 09:48 | 0.35 | 19.3333 | Kahramaa power interruption, the power module restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
361 | Sirti-WAN-R3-Ticket-334 | NA | 2026-05-23 | Sanket | Link Down | LAN Link down | Link Flapping | DUK-ENC06-CE-01 |  | Zone 80 | 25.3954062° 51.1985851° | Inside Doha | Critical | 2026-05-23 14:24 | 2026-05-23 14:26 | 2 | 2026-05-23 14:52 | 2026-05-23 14:55 | 3.45 | 31 | FLM replaced Ethernet cable and checked POE power connections | Completed | Maintainer | NA | N/a | Alarm Cleared | Khadar
362 | Sirti-WAN-R3-Ticket-335 | NA | 2026-05-24 | Aaqib | Link Down | LAN Link down | Link Auto Restored | COR-ENC07-CE-01 |  |  | 25.311996° 51.520.188° | Inside Doha | Critical | 2026-05-24 10:21 | 2026-05-24 10:22 | 1.5667 | 2026-05-24 10:22 | 2026-05-24 10:24 | 2.2 | 3.7667 | Link Auto restored after 3 min. | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
363 | Sirti-WAN-R3-Ticket-336 | NA | 2026-05-24 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage | P059C1-Enc04-UPE-01 P059C1-Enc04-CE-01 |  |  | 25.3653937° 51.4467471° | Outside Doha | Critical | 2026-05-24 11:19 | 2026-05-24 11:22 | 3.25 | 2026-05-24 11:22 | 2026-05-24 11:25 | 2.75 | 6 | khahrama Power Interruption | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Back Online | -
364 | Sirti-WAN-R3-Ticket-337 | NA | 2026-05-24 | Aaqib | CPU Temperature too high | High Temperature | AC not cooling, high temp | P007C2-ENC99-UPE-02 |  | Zone 54 | 25.2967109° 51.4488814° | Inside Doha | Major | 2026-05-24 13:24 | 2026-05-24 13:28 | 4 | 2026-05-24 14:23 | 2026-05-24 14:47 | 23.8 | 83.3833 | The faulty copper filter drier-15 was replaced due to a detected leak. The leak was repaired, the filter was replaced, and cleaning was completed as part of the maintenance work. AC is replaced with another AC unit. After testing, the air conditioning system was confirmed to be operating normally with proper cooling performance. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
365 | Sirti-WAN-R3-Ticket-338 | NA | 2026-05-25 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down | P023C2-ENC11-UPE-01 P023C2-ENC11-CE-01 |  |  | 25.325262° 51.329176° | Outside Doha | Critical | 2026-05-25 05:21 | 2026-05-25 05:27 | 5.5833 | 2026-05-25 05:27 | 2026-05-25 05:37 | 10.0833 | 15.6667 | Kahramaa power interruption, Devices restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
366 | Sirti-WAN-R3-Ticket-338 | NA | 2026-05-25 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down | P023C3-ENC21-UPE-01 P023C3-ENC21-CE-01 |  |  | 25.1750987° 51.3316767° | Outside Doha | Critical | 2026-05-25 05:21 | 2026-05-25 05:27 | 5.65 | 2026-05-25 05:27 | 2026-05-25 05:37 | 10.2333 | 15.8833 | Kahramaa power interruption, Devices restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
367 | Sirti-WAN-R3-Ticket-390 | NA | 2026-05-25 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | No Output from UPS | P005-ENC413-CE-01 |  | Zone 52 | 25.3203738° 51.4518769° | Outside Doha | Critical | 2026-05-25 12:39 | 2026-05-25 12:42 | 3.1167 | 2026-05-25 13:36 | 2026-05-25 14:39 | 63.8 | 120.2833 | UPS was not giving output. Device restored after bypassing UPS. | Completed | Non-maintainer | Defect | UPS | Devices Back Online | Irshad
368 | Sirti-WAN-R3-Ticket-340 | NA | 2026-05-25 | Abubaker | HARD_ERR | Equipment Error | Hardware error alarm on the Universal 100Gbit/s Line Service Processing Board | P007 SOC_TO_TCC_P004 Sec |  |  | 25.2942202° 51.4657002° | Inside Doha | Low | 2026-05-25 23:49 | 2026-05-26 | 10.8667 | 2026-05-26 | 2026-05-26 00:05 | 4.7667 | 15.6333 | Performed a cold reset for the board Z5UNS4 | Completed | Maintainer | N/a | N/a | Alarm Cleared | -
369 | Sirti-WAN-R3-Ticket-341 | NA | 2026-05-26 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down | P007C2-ENC99-CE-01 P007C2-ENC99-UPE-02 |  | Zone 54 | 25.2967109° 51.4488814° | Inside Doha | Critical | 2026-05-26 02:23 | 2026-05-26 02:34 | 11.4667 | 2026-05-26 02:34 | 2026-05-26 02:40 | 6.0333 | 17.5 | Kahramaa power interruption, Devices restored once the power recovered | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
370 | Sirti-WAN-R3-Ticket-342 | NA | 2026-05-27 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down | P023C2-ENC11-UPE-01 P023C2-ENC11-CE-01 |  |  | 25.18893° 51.32509° | Outside Doha | Critical | 2026-05-27 06:41 | 2026-05-27 06:44 | 3.3 | 2026-05-27 06:44 | 2026-05-27 08:02 | 77.3333 | 80.6333 | Kahramaa power interruption. Devices restored just FLM arrival to site. No action required by FLM | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
371 | Sirti-WAN-R3-Ticket-342 | NA | 2026-05-27 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down | P023C3-ENC21-UPE-01 P023C3-ENC21-CE-01 |  |  | 25.1750987° 51.3316767° | Outside Doha | Critical | 2026-05-27 06:41 | 2026-05-27 06:44 | 3.3 | 2026-05-27 06:44 | 2026-05-27 08:02 | 77.3333 | 80.6333 | Kahramaa power interruption. Devices restored just FLM arrival to site. No action required by FLM | Completed | Non-maintainer | 3rd Party | State Kahramaa | Devices Back Online | -
372 | Sirti-WAN-R3-Ticket-343 | NA | 2026-05-27 | Aaqib | Link Down | LAN Link down | LAN device was down due to high temperature | RAA-ENC01-CE-01 |  |  | 25.284123° 51.5558539° | Inside Doha | Critical | 2026-05-27 12:01 | 2026-05-27 12:07 | 6.0333 | 2026-05-27 12:32 | 2026-05-27 12:36 | 4.0667 | 35.1 | The 10G Link is conneceted to LAN device and the LAN device was down due to high temperature inside cabinet. | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Patrick
373 | Sirti-WAN-R3-Ticket-344 | NA | 2026-05-27 | Aaqib | CPU Temperature too high | High Temperature | A/C is not cooling | RAA-ENC01-UPE-01 |  |  | 25.284123° 51.5558539° | Inside Doha | Critical | 2026-05-27 12:06 | 2026-05-27 12:07 | 1.4667 | 2026-05-27 12:35 | 2026-05-27 12:36 | 1.0667 | 30.5333 | AC Team replaced comperossor relay , AC is working normally now | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
374 | Sirti-WAN-R3-Ticket-345 | NA | 2026-05-27 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C is not cooling | P011-ENC44-UPE-02 |  |  | 25.22292 51.57976 | Inside Doha | Critical | 2026-05-27 13:09 | 2026-05-27 13:14 | 4.55 | 2026-05-27 13:51 | 2026-05-27 13:59 | 7.5 | 49.55 | AC Team Maintaned the AC and restart it , now it is working and keeping under observation | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
375 | Sirti-WAN-R3-Ticket-346 | NA | 2026-05-27 | Aaqib | Link Down | LAN Link down | Link auto restored | P017C2-ENC01-CE-01 |  |  | 25.1702778° 51.4710278° | Inside Doha | Critical | 2026-05-27 13:32 | 2026-05-27 13:39 | 7.1167 | 2026-05-27 13:32 | 2026-05-27 14:40 | 67.8 | 67.8 | FLM replaced Ethernet cable connected to CE port GE1/1 | Completed | Maintainer | NA | N/a | Alarm Cleared | -
376 | Sirti-WAN-R3-Ticket-347 | NA | 2026-05-27 | Adel | Link Down | LAN Link down | Link is down due to QNBN fiber damage | 22FEB-ENC01-CE-01 |  |  | 25.2453756° 51.5148756° | Inside Doha | Critical | 2026-05-27 19:41 | 2026-05-27 19:45 | 4 | 2026-05-27 20:23 | 2026-05-28 16:39 | 1216.35 | 1258.2333 | Issue scalated to QNBN team, QNBN team shifted the link to a healthy fiber and the link recovered | Completed | Non-maintainer | 3rd Party | QNBN Fiber | Link is Up | Khadar
377 | Sirti-WAN-R3-Ticket-348 | NA | 2026-05-28 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C is not cooling | CRR-ENC30-UPE-02 |  |  | 25.268° 51.515° | Inside Doha | Critical | 2026-05-28 13:02 | 2026-05-28 13:06 | 4.4167 | 2026-05-28 14:50 | 2026-05-28 14:52 | 2.0333 | 109.85 | FLM team fill the R22 refrigrator gas and perform general servicing for the A/C system | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
378 | Sirti-WAN-R3-Ticket-349 | NA | 2026-05-28 | Aaqib | Temperature higher than Upper threshold | High Temperature | High Temperature inside the Cabinet and A/C compressor not working properly | P028C2-ENC25-UPE-01 |  |  | 25.2898333° 51.5151388° | Inside Doha | Critical | 2026-05-28 13:06 | 2026-05-28 13:10 | 3.6 | 2026-05-28 13:27 | 2026-05-28 13:30 | 3.2 | 24.05 | alarm auto cleared however the FLM team fixed the malfunctioning compressor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Eric
379 | Sirti-WAN-R3-Ticket-350 | NA | 2026-05-28 | Aaqib | Temperature higher than Upper threshold | High Temperature | Alarm Auto restored before FLM reached the site | P007C2-ENC01-UPE-01 |  |  | 25.2931613° 51.4894255° | Inside Doha | Critical | 2026-05-28 13:30 | 2026-05-28 13:33 | 3.4833 | 2026-05-28 13:24 | 2026-05-28 13:48 | 23.1667 | 17.8167 | we found the condenser pipe was leaking. The unit was opened and cleaned with chemicals and water. The copper condenser pipe was repaired by brazing, and a leakage test was done using nitrogen gas. Next, the condenser and evaporator were flushed with nitrogen gas and cleaned with chemicals. The AC parts were washed with water, serviced with a blower, and wiped with cloth towels. A vacuum pump was used to clean the system. We then filled the AC with R‑407C refrigerant gas, set the temperature, and cleaned the parts again with a blower and cloth towels. | Completed | Non-maintainer | Defect | AC | Alarm auto Cleared | Khadar
380 | Sirti-WAN-R3-Ticket-351 | NA | 2026-05-28 | Aaqib | Power Modules stopped working | Power alarm | Kharahma Outage is down | P007C2-ENC01-UPE-01 |  |  | 25.2931613° 51.4894255° | Inside Doha | Critical | 2026-05-28 14:45 | 2026-05-28 14:51 | 6.4167 | 2026-05-28 14:45 | 2026-05-28 16:28 | 103.4167 | 103.4167 | Kahramaa power interruption, alarms cleared once the power recovered | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
381 | Sirti-WAN-R3-Ticket-351 | NA | 2026-05-28 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down | P007C2-ENC01-UPE-01 P007C2-ENC01-CE-01 |  |  | 25.2931613° 51.4894255° | Inside Doha | Critical | 2026-05-28 14:45 | 2026-05-28 14:51 | 5.6167 | 2026-05-28 14:45 | 2026-05-28 15:24 | 38.1667 | 38.1667 | Kahramaa power interruption, alarms cleared once the power recovered | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
382 | Sirti-WAN-R3-Ticket-352 | NA | 2026-05-28 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | Kharahma Outage is down | P007C7P2-ENC26-CE-01 |  |  | 25.3062231° 51.4645491° | Inside Doha | Critical | 2026-05-28 17:49 | 2026-05-28 17:51 | 2.1333 | 2026-05-28 17:49 | 2026-05-28 17:58 | 9.2 | 9.2 | Kahramaa power interruption, alarms cleared once the power recovered | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
383 | Sirti-WAN-R3-Ticket-352 | NA | 2026-05-28 | Abubaker | Link Down | WAN Link down | Kharahma Outage is down | P007C7P2-ENC49-CE-01 |  |  | 25.3133081° 51.4633077° | Inside Doha | Critical | 2026-05-28 17:48 | 2026-05-28 17:58 | 9.65 | 2026-05-28 17:49 | 2026-05-28 18:41 | 52.0167 | 52.5333 | Link auto restored, checked the link health and ensured that the link is up and optical power level is OK and cleared the alarm manually | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
384 | Sirti-WAN-R3-Ticket-353 | NA | 2026-05-29 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | While performing PPM activity, the device got shut down | P019-ENC63-CE-01 |  |  | 25.5878055° 51.1144722° | Inside Doha | Critical | 2026-05-29 01:58 | 2026-05-29 01:59 | 1 | 2026-05-29 01:59 | 2026-05-29 02:02 | 2.9333 | 3.9333 | Device went down during PPM actvity | Completed | Non-maintainer | Planned Activity | PPM | Devices Back Online | Ghulam
385 | Sirti-WAN-R3-Ticket-354 | NA | 2026-05-29 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C was found off | RAA-ENC01-UPE-01 |  |  | 25.284123° 51.5558539° | Inside Doha | Critical | 2026-05-29 10:36 | 2026-05-29 10:41 | 5.4 | 2026-05-29 11:22 | 2026-05-29 11:26 | 3.9667 | 50.15 | AC starts cooling after restarting | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Irshad
386 | Sirti-WAN-R3-Ticket-355 | NA | 2026-05-29 | Abubaker | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling | P011-ENC44-UPE-02 |  | Zone 50 | 25.22292° 51.57976° | Inside Doha | Critical | 2026-05-29 10:52 | 2026-05-29 10:59 | 6.9 | 2026-05-29 10:52 | 2026-05-29 11:52 | 59.7667 | 59.7667 | Alarm Cleared before FLM reach the site however FLM team went to the site and restarted the A/C and compressor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Abuthahir
387 | Sirti-WAN-R3-Ticket-356 | NA | 2026-05-29 | Aaqib | Temperature higher than Upper threshold | High Temperature | 2 A/Cs are working but not cooling | P023C3-Enc21-UPE-01 |  | Zone 55 | 25.1750987° 51.3316767° | Outside Doha | Critical | 2026-05-29 12:07 | 2026-05-29 12:12 | 4.75 | 2026-05-29 13:03 | 2026-05-29 13:06 | 2.7667 | 58.3 | FLM opened the cabinet door and kept it open for a while to cool down the cabinet and clear the alarms and scheduled for A/C inspection and servicing | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Najeeb
388 | Sirti-WAN-R3-Ticket-357 | NA | 2026-05-29 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling | P003-ENC40-UPE-02 |  | Zone 66 | 25.3344995° 51.5180512° | Inside Doha | Critical | 2026-05-29 12:07 | 2026-05-29 12:14 | 6.4333 | 2026-05-29 12:58 | 2026-05-29 13:00 | 1.9333 | 52.7333 | FLM opened the cabinet door and kept it open for a while to cool down the cabinet and clear the alarms and scheduled for A/C inspection and servicing | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham
389 | Sirti-WAN-R3-Ticket-358 | NA | 2026-05-29 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling | 22FEB-ENC25-UPE-02 |  | Zone 34 | 25.31832397° 51.47088144° | Inside Doha | Critical | 2026-05-29 12:07 | 2026-05-29 12:12 | 4.5333 | 2026-05-29 12:07 | 2026-05-29 13:16 | 68.4333 | 68.4333 | Alarm Cleared before FLM reach the site however FLM team went to the site and restarted the A/C and compressor | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham
390 | Sirti-WAN-R3-Ticket-359 | NA | 2026-05-29 | Aaqib | CPU Temperature too high | High Temperature | Schema Under Salam Tech | P008C3-ENC01-UPE-01 |  |  | 25.2614822° 51.4801647° | Inside Doha | Critical | 2026-05-29 13:32 | 2026-05-29 13:36 | 4.5333 | 2026-05-29 13:32 | 2026-05-29 15:37 | 125.5 | 125.5 | Schema Under Salam Tech. Escalated to there team | Completed | Non-maintainer | 3rd Party | Salam Tech | Alarm Cleared | -
391 | Sirti-WAN-R3-Ticket-360 | NA | 2026-05-29 | Aaqib | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling | P010-ENC89-UPE-02 |  | Zone 91 | 25.1794434° 51.5014669° | Outside Doha | Critical | 2026-05-29 14:50 | 2026-05-29 14:52 | 2.8833 | 2026-05-29 15:28 | 2026-05-29 16:26 | 57.5667 | 96.0667 | Inspected the AC unit by checking the power cables and voltage supply, then cleaned the system thoroughly. Restarted the AC power and performed a general service. After servicing, the unit was tested and confirmed to be operating properly with good cooling performance, and the compressor is now functioning correctly and providing cooling as expected | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Hicham / Khadar
392 | Sirti-WAN-R3-Ticket-361 | NA | 2026-05-29 | Abubaker | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling | P006-ENC02-UPE-01 P006-ENC02-UPE-02 |  | Zone 56 | 25.2190399° 51.4369501° | Inside Doha | Critical | 2026-05-29 15:10 | 2026-05-29 15:16 | 6.3167 | 2026-05-29 15:10 | 2026-05-29 16:47 | 97.35 | 97.35 | Inspected the AC unit by checking the power cables and voltage supply, and found that the AC compressor was not responding. Restarted the AC power and carried out a general service. After servicing, the unit was tested and confirmed to be working properly with good cooling performance. The AC compressor is now functioning properly | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar
393 | Sirti-WAN-R3-Ticket-362 | NA | 2026-05-30 | Sanket/Adel | Communication betweeen NMS and NE is Abnormal | Device Down | No power at WAN cabinet | P060-ENC125-CE-GME-01 |  |  |  | Outside Doha | Critical | 2026-05-30 06:07 | 2026-05-30 06:13 | 5.2 | 2026-05-30 06:57 | 2026-05-30 08:47 | 110 | 159.6167 | FLM connected portable generator temporary till they find the FP location , then FLM switched on tripped CB at FP | Completed | Maintainer | N/a | N/a | Devices Back Online | Hicham
394 | Sirti-WAN-R3-Ticket-363 | NA | 2026-05-30 | Sanket | Link Down | LAN Link down | Link auto restored (GE 1/0/9 towards Local Node) | SAL-ENC63-CE-01 |  |  | 24.8301249° 50.8705931° | Outside Doha | Critical | 2026-05-30 23:21 | 2026-05-30 23:28 | 7.1 | 2026-05-30 23:49 | 2026-05-30 23:50 | 1 | 29.3167 | Alarm Auto restored before FLM reached the site (The Link is down towards LAN) | Completed | Non-maintainer | N/a | N/a | Alarm Cleared | -
395 | Sirti-WAN-R3-Ticket-364 | NA | 2026-05-31 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | While performing PPM activity, the device got shut down | P060-ENC179-UPE-02 P060-ENC179-CE-GME-01 |  | Zone 70 | 25.63950 51.49451 | Outside Doha | Critical | 2026-05-31 01:01 | 2026-05-31 01:02 | 1 | 2026-05-31 01:03 | 2026-05-31 01:06 | 2.5167 | 4.5167 | While performing PPM activity, the device got shut down | Completed | Non-maintainer | Planned Activity | PPM | Devices Back Online | Ghulam
396 | Sirti-WAN-R3-Ticket-365 | NA | 2026-05-31 | Sanket | Communication betweeen NMS and NE is Abnormal | Device Down | During the PPM activity at site P060-ENC179, it was observed that the main power cable lugs require proper tightening and fixing | P060-ENC179-UPE-02 P060-ENC179-CE-GME-01 |  | Zone 70 | 25.63950 51.49451 | Outside Doha | Critical | 2026-05-31 02:07 | 2026-05-31 02:08 | 1 | 2026-05-31 02:14 | 2026-05-31 02:15 | 0.81667 | 7.8333 | During the PPM activity at site P060-ENC17, it was observed that the main power cable lugs require proper tightening and fixing.Then, we removed the main power cable, installed the cable lugs, fixed them properly | Completed | Non-maintainer | Planned Activity | PPM | Devices Back Online | Ghulam
397 | Sirti-WAN-R3-Ticket-366 | NA | 2026-05-31 | Sanket | Link Down | LAN Link down | Fiber Patch chord issue at Port XG 0/1/7 towards 17025-SR1-ASW-E12-10 | P003-ENC05-CE-01-DGME01 |  | Zone 66 | 25.3811922° 51.5208128° | Inside Doha | Critical | 2026-05-31 04:40 | 2026-05-31 04:50 | 10.0833 | 2026-05-31 05:33 | 2026-05-31 06:11 | 37.55 | 91.1667 | Verified that the LC/PC-to-LC/PC 3-meter fiber patch cord was faulty. Replaced it with a new fiber patch cord, and the link is now up and stable | Completed | Maintainer | N/a | N/a | Alarm Cleared | Umair
398 | Sirti-WAN-R3-Ticket-371 | NA | 2026-05-31 | Adel | Temperature higher than Upper threshold | High Temperature | A/C is working but not cooling | P011-ENC44-UPE-02 |  | Zone 50 | 25.22292° 51.57976° | Inside Doha | Critical | 2026-05-31 13:49 | 2026-05-31 13:52 | 3 | 2026-05-31 14:31 | 2026-05-31 14:34 | 3.1833 | 45.1833 | FLM team went to the site and restarted the A/C and compressor then the cabinet Temp become normal and then replaced the 40+5 capacitor. The unit is now operating normally and performing well | Completed | Non-maintainer | Defect | AC | Alarm Cleared | Khadar / Eric
399 | Sirti-WAN-R3-Ticket-372 | NA | 2026-05-31 | Abubaker | Link Down | WAN link down | Ethernet loose connection for the port port Gi 0/0/12 | P006-ENC17-CE-01 |  | Zone 56 | 25.19542° 51.454° | Inside Doha | Critical | 2026-05-31 18:32 | 2026-05-31 18:41 | 9.3167 | 2026-05-31 20:22 | 2026-05-31 20:24 | 2.1833 | 112.0667 | Cleaned the Ethernet cable and connected it properly to the switch port Gi 0/0/12 | Completed | Maintainer | N/a | N/a | Alarm Cleared | Hassan
400 | Sirti-WAN-R3-Ticket-373 | NA | 2026-06-01 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | ITSQ activity on site | P040-CPE01-ENC01-DSW |  |  | 25.179715° 51.408779° | Inside Doha | Critical | 2026-06-01 08:59 | 2026-06-01 09:04 | 5 | 2026-06-01 09:30 | 2026-06-01 09:39 | 8.8833 | 39.6833 | issue is escalated to ITSQ via mail , FLM visisted and found ITSQ team is working at cabinet | Completed | Non-maintainer | 3rd Party | ITSQ Contractor | Alarm Cleared | Hicham
401 | Sirti-WAN-R3-Ticket-374 | NA | 2026-06-01 | Adel | power module stopped working | power alarm | kahromaa power inturruption | P003-ENC40-UPE-02 |  |  | 25.3344995° 51.5180512° | Inside Doha | Critical | 2026-06-01 10:22 | 2026-06-01 10:26 | 4 | 2026-06-01 11:30 | 2026-06-01 11:49 | 19 | 87.5 | Kahromaa power inturruption alarm is auto restored , flm did not visit in summer time | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared
402 | Sirti-WAN-R3-Ticket-375 | NA | 2026-06-01 | Adel | link down | LAN Link down | LAN switch was found down due to breaker tripped | P028C2-ENC-07-CE-01.omc.local |  | Zone 27 | 25.2827572° 51.5448455° | Inside Doha | Critical | 2026-06-01 09:57 | 2026-06-01 10:03 | 6 | 2026-06-01 16:34 | 2026-06-01 16:42 | 8.2 | 404.5167 | breaker turned ON and power is restored, the LAN switch become up and link restored | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Irshad
403 | Sirti-WAN-R3-Ticket-376 | NA | 2026-06-01 | Adel | optical model temprature too high | High Temperature | A/C is fans are not working, Temprature is high inside the cabinet | P059C1-ENC04-CE-01 P059C1-ENC04-UPE-01 |  | Zone 71 | 25.3653937° 51.4467471° | Outside Doha | Critical | 2026-06-01 13:04 | 2026-06-01 13:06 | 2 | 2026-06-01 16:30 | 2026-06-01 16:31 | 1.2 | 207.5667 | General servicing of both AC units was carried out, including cleaning and inspection of filters and coils. After completion of service, both AC units were started and tested.Both AC units are now operating normally with proper cooling performance. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Najeeb
404 | Sirti-WAN-R3-Ticket-377 | NA | 2026-06-01 | Adel | CPU Temperature too high | High Temperature | Compressor faulty | P006-ENC02-UPE-01 |  | Zone 56 | 25.2190399° 51.4369501° | Inside Doha | Critical | 2026-06-01 13:56 | 2026-06-01 13:58 | 3 | 2026-06-01 16:06 | 2026-06-01 16:12 | 5.5667 | 136.2333 | The faulty AC compressor at cabinet P06-ENC-02 was replaced with a new LG unit, the condenser and evaporator were thoroughly cleaned, new filter, capillary pipe, and capacitor were installed, R-22 gas was charged, and after servicing, the AC was tested and confirmed to be cooling properly. | Completed | Non-maintainer | Environmental | Heat summer | Alarm Cleared | Sanjeewa
405 | Sirti-WAN-R3-Ticket-378 | NA | 2026-06-01 | Abubaker | Link Down | LAN link down | Port Auto restored before FLM reach the site | DUK-ENC04-CE-01 |  |  | 25.3809325° 51.2215135° | Outside Doha | Critical | 2026-01-06 16:40 | 2026-01-06 16:50 | 10.3667 | 2026-01-06 16:40 | 2026-01-06 16:57 | 17.6667 | 17.6667 | Link Auto restored before FLM reached the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Alarm Cleared | -
406 | Sirti-WAN-R3-Ticket-379 | NA | 2026-06-01 | Abubaker | Communication betweeen NMS and NE is Abnormal | Device Down | kahromaa power inturruption | DUK-ENC30-CE-01 |  |  | 25.4637854° 50.930279° | Outside Doha | Critical | 2026-01-06 20:57 | 2026-01-06 21:01 | 4.1 | 2026-01-06 20:57 | 2026-01-06 21:04 | 7.5833 | 7.5833 | Kahromaa power inturruption device flapped and auto restored before FLM reaching the site | Completed | Non-maintainer | 3rd Party | State Kahramaa | Device Back Online | -
407 | Sirti-WAN-R3-Ticket-380 | NA | 2026-06-02 | Aaqib | Link Down | LAN link down | SFP was stuck and was not functioning | P003-ENC05-CE-01-DGME01 |  |  | 25.3811922° 51.5208128° | Inside Doha | Critical | 2026-02-06 00:30 | 2026-02-06 00:33 | 3.4 | 2026-02-06 01:17 | 2026-02-06 01:39 | 21.25 | 68.8667 | SFP was stuck. Link was restored after JIJO at LAN switch side. | Completed | Non-maintainer | N/a | N/a | Alarm Cleared | Hassan
408 | Sirti-WAN-R3-Ticket-381 | NA | 2026-06-02 | Aaqib | Communication betweeen NMS and NE is Abnormal | Device Down | MCB was found tripped | P028C2-ENC07-CE-01 |  |  | 25.2827572° 51.5448455° | Inside Doha | Critical | 2026-02-06 02:25 | 2026-02-06 02:29 | 4.45 | 2026-02-06 03:09 | 2026-02-06 03:18 | 9 | 53.4167 | Device restored after turning ON MCB inside cabinet | Completed | Maintainer | N/a | N/a | Device Back Online | Hichem
409 | Sirti-WAN-R3-Ticket-382 | NA | 2026-06-02 | Aaqib | Link Down | LAN link down | Dirty UPC connector causing Link down | P003-ENC05-CE-01-DGME01 |  |  | 25.3811922° 51.5208128° | Inside Doha | Critical | 2026-02-06 03:19 | 2026-02-06 03:22 | 2.3833 | 2026-02-06 04:23 | 2026-02-06 04:36 | 13.2167 | 76.7167 | The fiber connector was dirty. Team cleaned it and reinserted the connector. After which the link restored. | Completed | Non-maintainer | N/a | N/a | Alarm Cleared | Umair
410 | Sirti-WAN-R3-Ticket-383 | NA | 2026-06-02 | Aaqib | Link Down | LAN link down | RJ45 Connector was dirty and cable not propelry routed | DUK-ENC04-CE-01 |  |  | 25.3809325° 51.2215135° | Outside Doha | Critical | 2026-02-06 04:43 | 2026-02-06 04:53 | 9.8333 | 2026-02-06 05:26 | 2026-02-06 05:41 | 15.6167 | 57.8833 | Connector was dirty. Team just plug out, clean it and reroute and insert again after which link restored | Completed | Maintainer | N/a | N/a | Alarm Cleared | Ghulam
411 | Sirti-WAN-R3-Ticket-384 | NA | 2026-06-02 | Adel | Communication betweeen NMS and NE is Abnormal | Device Down | No power at WAN cabinet | P059C1-ENC20-CE-01 |  |  | 25.44194931° 51.41112813° | Outside Doha | Critical | 2026-02-06 09:37 | 2026-02-06 09:40 | 3 | 2026-02-06 16:44 | 2026-02-06 17:27 | 43.3833 | 469.9 | FLM switched on tripped CB at FP | Completed | Non-maintainer | Environmental | Heat summer | Device Back Online | Sanjeewa
412 | Sirti-WAN-R3-Ticket-385 | NA | 2026-06-02 | Adel | CRC Error alarm notification | CRC Alarm on port 2/0/0 | errors oncounted on port | P003-ENC40-UPE-02 |  |  | 25.3344995° 51.5180512° | Outside Doha | Critical | 2026-02-06 14:50 | 2026-02-06 14:55 | 5 | 2026-02-06 15:40 | 2026-02-06 16:09 | 28.9333 | 78.6 | FLM replaced ER SFP at IE5000-6009 port TE1/26 | Completed | maintainer | N/a | N/a | Alarm Cleared | Najeeb
413 | Sirti-WAN-R3-Ticket-386 | NA | 2026-06-03 | Adel | Link Down | Link Down to UPS | Planned activity with huawei team for UPS PPM inside battery room | P007-ENC-NMS-SW-01 |  |  | 25.2942202° 51.4657002° | Inside Doha | Critical | 2026-03-06 08:52 | 2026-03-06 08:53 | 1 | 2026-03-06 08:52 | 2026-03-06 08:58 | 6.2 | 6.2 | Planned activity with huawei team for UPS PPM inside battery room | Completed | Non-maintainer | N/a | N/a | Alarm Cleared | Patric
414 | Sirti-WAN-R3-Ticket-387 | NA
415 | Sirti-WAN-R3-Ticket-388 | NA
416 | Sirti-WAN-R3-Ticket-389 | NA
417 | Sirti-WAN-R3-Ticket-390 | NA
418 | Sirti-WAN-R3-Ticket-391 | NA
419 | Sirti-WAN-R3-Ticket-392 | NA
420 | Sirti-WAN-R3-Ticket-393 | NA
421 | Sirti-WAN-R3-Ticket-394 | NA
422 | Sirti-WAN-R3-Ticket-395 | NA
423 | Sirti-WAN-R3-Ticket-396 | NA
424 | Sirti-WAN-R3-Ticket-397 | NA
425 | Sirti-WAN-R3-Ticket-398 | NA
426 | Sirti-WAN-R3-Ticket-399 | NA
427 | Sirti-WAN-R3-Ticket-400 | NA
428 | Sirti-WAN-R3-Ticket-401 | NA

## Legend
Maintainer | N/a | N/a |  |  | Maintainer | N/a | N/a
Non-maintainer | Access | no keys, police not allow |  |  | Non-maintainer | Access | no keys, police not allow
| Environmental | flooding, dust storm |  |  |  | Environmental | flooding, dust storm
| 3rd party | car crash, Bin omran contractor damage |  |  |  | 3rd party | car crash, Bin omran contractor damage
|  |  | Inside Doha | Critical | fault showed on system | team dispatched |  | reach site | finish repair
|  |  | Outside Doha | High
Medium
Low